## Full Disclaimer
Insert Your Logo Here
Full Disclaimer
This tool is aimed at assisting users in decision-making by providing analysis based on various assumptions and a variety of factors. While an effort has been made to use accurate assumptions and factors in developing this tool, COOPER LIGHTING MAKES NO WARRANTY OR GUARANTEE, EXPRESS OR IMPLIED, (i) THAT THE RESULTS DESCRIBED HEREIN WILL BE OBTAINED UNDER END-USE CONDITIONS, OR (ii) AS TO THE EFFECTIVENESS, SAFETY OR APPROPRIATENESS OF ANY DESIGN INCORPORATING COOPER LIGHTING MATERIALS, PRODUCTS, USES, RECOMMENDATIONS OR ADVICE. IN NO EVENT SHALL COOPER LIGHTING BE RESPONSIBLE FOR ANY LOSS RESULTING FROM ANY USE OF THIS TOOL.
Each user bears full responsibility for making its own determination as to the suitability of Cooper Lighting’s materials, products, recommendations, analyses, or advice for its own particular use. Each user must identify and perform all tests and analyses necessary to assure that its products and designs incorporating Cooper Lighting material or products will be safe and suitable for use under end-use conditions. Nothing in this or any other document, nor any oral recommendation or advice, shall be deemed to alter, vary, supersede, or waive any provisions of this Disclaimer, unless any such modification is specifically agreed to in writing signed by Cooper Lighting. No statement contained herein concerning a possible or suggested use of any material, product or design is intended, or should be construed, to grant any license under any patent or other intellectual property right of Cooper Lighting or any it subsidiaries or affiliates covering such use or design, or as a recommendation for the use of such material, product or design in the infringement of any patent or other intellectual property right.
Questions about models or assumptions used in these calculations may be addressed to:
Cooper Lighting
1121 Highway 74 South
Peachtree City, GA. 30269
Tel: (770) 486-4800
E-mail: EnergySolutions@cooperlighting.com

## HOME
Insert Logo Here |  | Energy Efficiency Tool Kit
Our world is increasingly recognizing the importance of environmental sustainability and efficiency in building design. Good business is cost-conscious and environmentally responsible while driving more to the bottom line through increased productivity and a smaller carbon footprint.
The Energy Efficiency Tool Kit includes calculators to helps you to make informed decisions when considering an energy efficient and sustainable lighting system.
|  | Payback Analysis |  | 10 Year Maintenance Cost Estimator
|  | Payback Analysis: Controls |  | Maintenance Cost Estimator
|  | Payback Analysis: Multiple System |  | Maintenance Factors
|  | Payback Analysis: Multiple Luminaires |  | Productivity Impact of Lighting Retrofit
|  | Energy Analysis |  | Impact of Lighting Retrofit on HVAC Costs
| NEW | Retrofit Opportunity Estimator |  | F-BAY System Comparison
|  | Cost of Waiting |  | Stair Lite
|  | Lighting Power Density (w/sqft) & EZ EPAct |  | Tips for a Successful Energy Audit
| NEW | Lighting Power Density (ASHRAE 90.1 2004) |  | Lighting System Audit Forms
| NEW | EPAct Certification Form |  |  | Site Background
|  | Environmental Impact |  |  | Fixture Information
|  | Scotopic/Photopic Impact |  |  | Fixture Detail
|  | Scotopic/Photopic Impact on Two Systems |  | Retrofit Luminaire Selector
|  | Coefficients of Utilization Table | NEW | Target Efficacy Rating (Revised LER)
|  | Luminaire Count Estimator |  | Input Watt Finder
|  | Common Footcandle Recommendations |  | Cash Flow Benefit of Financing
|  | Footcandle Estimator |  | Helpful Website Links
Maintained Illumination over System Life
Additional Step Up tools - including an EPAct calculator and Step Up Payback Proposal Program - are available by clicking the Step Up logo.
v2.3.8 Copyright of Cooper Lighting 2007 | [5 empty] | Click Here for the full Energy Efficiency Tool Kit Disclaimer
Return to TOP |  |  |  |  | 6082009

## Payback Analysis
Insert Logo Here
Lighting System Payback Analysis
Input
Output
Customer Information |  |  | Facility Information
Project Name: |  |  | Area (sq. ft.)
Cost Per kWh
Contact: |  |  | Annual Operating Hrs
|  |  | Sales Tax (%) | 0%
System Information |  | Existing |  | Proposed
Luminaire Description
Input Watts Per Luminaire
Quantity
| System Watts | 0 |  | 0
| System kW | 0 |  | 0
| Annual kWh | 0 |  | 0
| Annual Energy Costs | 0 |  | 0
| Monthly Costs | 0 |  | 0
Per Luminaire Cost
| Total System Cost |  |  | 0
Labor/Materials/Disposal (Lot Price)
| Per Luminaire Rebate/Incentive |  |  | 0
| Total System Rebate/Incentive |  |  | 0
| Total Contract Price |  |  | 0
Payback Analysis
Watts Per Square Foot
| Annual Energy Savings |  |  | 0
| Cost of Waiting (Monthly) |  |  | 0
| Simple Payback (Years) |  |  | #DIV/0!
| IRR (%) |  |  | #DIV/0!
| Five Year Energy Cash Flow |  |  | 0
Note: These are estimated savings only. These annual and monthly savings are based on a number of variables and assumptions that could change over time. The actual savings derived by your firm may be higher or lower.
Return to TOP
|  | Existing | Proposed
Return to HOME |  | 0 | 0
Annual Energy Savings

## NPV Disc (hidden)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
1% | 0.99 | 0.98 | 0.971 | 0.961 | 0.951 | 0.942 | 0.933 | 0.923 | 0.914 | 0.905 | 0.896 | 0.887 | 0.879 | 0.87 | 0.861 | 0.853 | 0.844 | 0.836 | 0.828 | 0.82 | 0.811 | 0.803 | 0.795 | 0.788 | 0.78 | 0.772 | 0.764 | 0.757 | 0.749 | 0.742
2% | 0.98 | 0.961 | 0.942 | 0.924 | 0.906 | 0.888 | 0.871 | 0.853 | 0.837 | 0.82 | 0.804 | 0.788 | 0.773 | 0.758 | 0.743 | 0.728 | 0.714 | 0.7 | 0.686 | 0.673 | 0.66 | 0.647 | 0.634 | 0.622 | 0.61 | 0.598 | 0.586 | 0.574 | 0.563 | 0.552
3% | 0.971 | 0.943 | 0.915 | 0.888 | 0.863 | 0.837 | 0.813 | 0.789 | 0.766 | 0.744 | 0.722 | 0.701 | 0.681 | 0.661 | 0.642 | 0.623 | 0.605 | 0.587 | 0.57 | 0.554 | 0.538 | 0.522 | 0.507 | 0.492 | 0.478 | 0.464 | 0.45 | 0.437 | 0.424 | 0.412
4% | 0.962 | 0.925 | 0.889 | 0.855 | 0.822 | 0.79 | 0.76 | 0.731 | 0.703 | 0.676 | 0.65 | 0.625 | 0.601 | 0.577 | 0.555 | 0.534 | 0.513 | 0.494 | 0.475 | 0.456 | 0.439 | 0.422 | 0.406 | 0.39 | 0.375 | 0.361 | 0.347 | 0.333 | 0.321 | 0.308
5% | 0.952 | 0.907 | 0.864 | 0.823 | 0.784 | 0.746 | 0.711 | 0.677 | 0.645 | 0.614 | 0.585 | 0.557 | 0.53 | 0.505 | 0.481 | 0.458 | 0.436 | 0.416 | 0.396 | 0.377 | 0.359 | 0.342 | 0.326 | 0.31 | 0.295 | 0.281 | 0.268 | 0.255 | 0.243 | 0.231
6% | 0.943 | 0.89 | 0.84 | 0.792 | 0.747 | 0.705 | 0.665 | 0.627 | 0.592 | 0.558 | 0.527 | 0.497 | 0.469 | 0.442 | 0.417 | 0.394 | 0.371 | 0.35 | 0.331 | 0.312 | 0.294 | 0.278 | 0.262 | 0.247 | 0.233 | 0.22 | 0.207 | 0.196 | 0.185 | 0.174
7% | 0.935 | 0.873 | 0.816 | 0.763 | 0.713 | 0.666 | 0.623 | 0.582 | 0.544 | 0.508 | 0.475 | 0.444 | 0.415 | 0.388 | 0.362 | 0.339 | 0.317 | 0.296 | 0.277 | 0.258 | 0.242 | 0.226 | 0.211 | 0.197 | 0.184 | 0.172 | 0.161 | 0.15 | 0.141 | 0.131
8% | 0.926 | 0.857 | 0.794 | 0.735 | 0.681 | 0.63 | 0.583 | 0.54 | 0.5 | 0.463 | 0.429 | 0.397 | 0.368 | 0.34 | 0.315 | 0.292 | 0.27 | 0.25 | 0.232 | 0.215 | 0.199 | 0.184 | 0.17 | 0.158 | 0.146 | 0.135 | 0.125 | 0.116 | 0.107 | 0.099
9% | 0.917 | 0.842 | 0.772 | 0.708 | 0.65 | 0.596 | 0.547 | 0.502 | 0.46 | 0.422 | 0.388 | 0.356 | 0.326 | 0.299 | 0.275 | 0.252 | 0.231 | 0.212 | 0.194 | 0.178 | 0.164 | 0.15 | 0.138 | 0.126 | 0.116 | 0.106 | 0.098 | 0.09 | 0.082 | 0.075
10% | 0.909 | 0.826 | 0.751 | 0.683 | 0.621 | 0.564 | 0.513 | 0.467 | 0.424 | 0.386 | 0.35 | 0.319 | 0.29 | 0.263 | 0.239 | 0.218 | 0.198 | 0.18 | 0.164 | 0.149 | 0.135 | 0.123 | 0.112 | 0.102 | 0.092 | 0.084 | 0.076 | 0.069 | 0.063 | 0.057
11% | 0.901 | 0.812 | 0.731 | 0.659 | 0.593 | 0.535 | 0.482 | 0.434 | 0.391 | 0.352 | 0.317 | 0.286 | 0.258 | 0.232 | 0.209 | 0.188 | 0.17 | 0.153 | 0.138 | 0.124 | 0.112 | 0.101 | 0.091 | 0.082 | 0.074 | 0.066 | 0.06 | 0.054 | 0.048 | 0.044
12% | 0.893 | 0.797 | 0.712 | 0.636 | 0.567 | 0.507 | 0.452 | 0.404 | 0.361 | 0.322 | 0.287 | 0.257 | 0.229 | 0.205 | 0.183 | 0.163 | 0.146 | 0.13 | 0.116 | 0.104 | 0.093 | 0.083 | 0.074 | 0.066 | 0.059 | 0.053 | 0.047 | 0.042 | 0.037 | 0.033
13% | 0.885 | 0.783 | 0.693 | 0.613 | 0.543 | 0.48 | 0.425 | 0.376 | 0.333 | 0.295 | 0.261 | 0.231 | 0.204 | 0.181 | 0.16 | 0.141 | 0.125 | 0.111 | 0.098 | 0.087 | 0.077 | 0.068 | 0.06 | 0.053 | 0.047 | 0.042 | 0.037 | 0.033 | 0.029 | 0.026
14% | 0.877 | 0.769 | 0.675 | 0.592 | 0.519 | 0.456 | 0.4 | 0.351 | 0.308 | 0.27 | 0.237 | 0.208 | 0.182 | 0.16 | 0.14 | 0.123 | 0.108 | 0.095 | 0.083 | 0.073 | 0.064 | 0.056 | 0.049 | 0.043 | 0.038 | 0.033 | 0.029 | 0.026 | 0.022 | 0.02
15% | 0.87 | 0.756 | 0.658 | 0.572 | 0.497 | 0.432 | 0.376 | 0.327 | 0.284 | 0.247 | 0.215 | 0.187 | 0.163 | 0.141 | 0.123 | 0.107 | 0.093 | 0.081 | 0.07 | 0.061 | 0.053 | 0.046 | 0.04 | 0.035 | 0.03 | 0.026 | 0.023 | 0.02 | 0.017 | 0.015

## Payback wControls
Insert Logo Here
Lighting System Payback Analysis
Input | Dimming Option
Output
Customer Information |  |  | Facility Information
Project Name: |  |  | Area (sq. ft.)
Cost Per kWh
Contact: |  |  | Annual Operating Hours
|  |  | Sales Tax (%) | 8.75%
System Information |  | Existing |  | Proposed
Luminaire Description
Input Watts Per Luminaire
Quantity
Lighting Controls | Quantity w/Lighting Controls
| % Annual Operating Hours Controlled | 0% |  | 0%
| % of Time Fixtures are OFF | 0% |  | 0%
| System Watts | 0 |  | 0
| System kW | 0 |  | 0
| Annual kWh | 0 |  | 0
| Annual Energy Costs | 0 |  | 0
| Monthly Costs | 0 |  | 0
Per Luminaire Cost
| Total System Cost |  |  | 0
Labor/Materials/Disposal (Lot Price)
Per Luminaire Rebate/Incentive
| Total System Rebate/Incentive |  |  | 0
| Total Contract Price |  |  | 0
Payback Analysis
| Watts Per Square Foot | #DIV/0! |  | #DIV/0!
| Annual Energy Savings |  |  | 0
| Cost of Waiting (Monthly) |  |  | 0
| Simple Payback (Years) |  |  | #DIV/0!
| IRR (%) |  |  | #DIV/0!
| Five Year Energy Cash Flow |  |  | 0
Note: These are estimated savings only. These annual and monthly savings are based on a number of variables and assumptions that could change over time. The actual savings derived may be higher or lower.
Return to TOP |  |  |  | 4232009
Return to HOME
|  | Existing |  | Proposed
| Annual Energy Costs | 0 |  | 0
Annual Energy Savings
Please Select
0%
10%
20%
30%
40%
50%
60%
70%
80%
90%
100%
Note on C19: If there are controls on the system enter the quantity of luminaires equipped with the controls. If there are no controls, field should have a zero.
Note on C20: This would be 100% if every fixture was controlled all the time. If there were times in the day that the fixtures were taken off of control you would calcuate % and select appropriate number.
Note on C21: Enter the percent of time the luminaires that will be turned off by the sensor. The balance (%) represents the time the luminaires are turned on.

## Payback MultSys
Insert Logo Here
Lighting System Payback Analysis:
Input | Multiple System Comparison
Output
Customer Information | [5 empty] | Facility Information
Project Name: |  |  |  |  | Area (sq. ft.)
Cost Per kWh
Contact: |  |  |  |  | Annual Operating Hours
[5 empty] | Sales Tax (%) |  | 8.75%
System Information |  | Existing |  | Proposed (1) | Proposed (2) |  | Proposed (3)
Luminaire Description
Input Watts Per Luminaire
Quantity
Lighting Controls | Quantity w/Lighting Controls
| % Annual Operating Hours Controlled | 0% |  | 0% | 0% |  | 0%
| % Light Output Controlled | 0% |  | 0% | 0% |  | 0%
| System Watts | 0 |  | 0 | 0 |  | 0
| System kW | 0 |  | 0 | 0 |  | 0
| Annual kWh | 0 |  | 0 | 0 |  | 0
| Annual Energy Costs | 0 |  | 0 | 0 |  | 0
| Monthly Costs | 0 |  | 0 | 0 |  | 0
Per Luminaire Cost
| Total System Cost |  |  | 0 | 0 |  | 0
| Labor/Materials/Disposal (Lot Price) |  |  | 0 | 0
Total Project Cost
| Per Luminaire Rebate/Incentive |  |  | 0 | 0 |  | 0
| Total System Rebate/Incentive |  |  | 0 | 0 |  | 0
| Total Contract Price |  |  | 0 | 0 |  | 0
Payback Analysis
| Watts Per Square Foot | #DIV/0! |  | #DIV/0!
| Annual Energy Savings |  |  | 0
| Cost of Waiting (Monthly) |  |  | 0
| Simple Payback (Years) |  |  | #DIV/0!
| IRR (%) |  |  | #DIV/0!
| Five Year Energy Cash Flow |  |  | 0
| Cost of Capital (%) | Please Select
| Net Present Value |  |  | #N/A
Note: These are estimated savings only. These annual and monthly savings are based on a number of variables and assumptions that could change over time. The actual savings derived may be higher or lower.
Return to TOP
Return to HOME
|  | Existing |  | Proposed (1) | Proposed (2) |  | Proposed (3)
| Annual Energy Costs | 0 | 0 | 0 | 0 |  | 0 | 0
| Annual Energy Savings |  |  | 0
| 0% | Please Select |  |  |  |  | Proposed 1 |  | Year One | Year Two | Year Three | Year Four | Year Five | NPV | NPV Index
| 10% | 0% |  |  |  |  | Discount |  | #N/A | #N/A | #N/A | #N/A | #N/A
| 20% | 1% |  |  |  |  | 0
| 30% | 2% |  |  |  |  | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 40% | 3%
| 50% | 4%
| 60% | 5% |  |  |  |  | Proposed 2 |  | Year One | Year Two | Year Three | Year Four | Year Five | NPV | NPV Index
| 70% | 6% |  |  |  |  | Discount |  | #N/A | #N/A | #N/A | #N/A | #N/A
| 80% | 7% |  |  |  |  | 0
| 90% | 8% | [6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 100% | 9%
10%
|  | 11% |  |  |  |  | Proposed 3 |  | Year One | Year Two | Year Three | Year Four | Year Five | NPV | NPV Index
|  | 12% |  |  |  |  | Discount |  | #N/A | #N/A | #N/A | #N/A | #N/A
|  | 13% |  |  |  |  | 0
|  | 14% | [6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
15%
Note on C19: If there are controls on the system enter the quantity of luminaires equipped with the controls. If there are no controls, field should have a zero.
Note on C21: Enter the percent of light output of the luminaires that will be controlled. The balance (%) represents the light output of the luminaires when controls are active.

## Payback MultLuminaires
Insert Logo Here |  | Lighting System Payback Analysis: Multiple Proposed Luminaires
Input
Output
Customer Information | [6 empty] | Facility Information
Project Name: | [5 empty] | Area (sq. ft.)
Cost Per kWh
Contact: | [5 empty] | Annual Operating Hours
[6 empty] | Sales Tax (%) |  | 8.75%
System Information |  |  | Existing |  | Luminaire (1) | Luminaire (2) |  | Luminaire (3) |  | Total Proposed
Luminaire Description
Input Watts Per Luminaire
Quantity
Lighting Controls | Quantity w/Lighting Controls
| % Annual Operating Hours Controlled |  | 0% |  | 0% | 0% |  | 0%
| % Light Output Controlled |  | 0% |  | 0% | 0% |  | 0%
| System Watts |  | 0 |  | 0 | 0 |  | 0 |  | 0
| System kW |  | 0 |  | 0 | 0 |  | 0 |  | 0
| Annual kWh |  | 0 |  | 0 | 0 |  | 0 |  | 0
| Annual Energy Costs |  | 0 |  | 0 | 0 |  | 0 |  | 0
| Monthly Costs |  | 0 |  | 0 | 0 |  | 0 |  | 0
Per Luminaire Cost
| Total System Cost |  |  |  | 0 | 0 |  | 0 |  | 0
| Labor/Materials/Disposal (Lot Price) | [8 empty] | 0
| Total Project Cost | [8 empty] | 0
Per Luminaire Rebate/Incentive
| Total System Rebate/Incentive |  |  |  | 0 | 0 |  | 0 |  | 0
| Total Contract Price | [8 empty] | 0
Payback Analysis
| Watts Per Square Foot |  | #DIV/0! | [6 empty] | #DIV/0!
| Annual Energy Savings | [8 empty] | 0
| Cost of Waiting (Monthly) | [8 empty] | 0
| Simple Payback (Years) | [8 empty] | #DIV/0!
| IRR (%) | [8 empty] | #DIV/0!
| Five Year Energy Cash Flow | [8 empty] | 0
| Cost of Capital (%) | [8 empty] | Please Select
| Net Present Value | [8 empty] | #N/A
Note: These are estimated savings only. These annual and monthly savings are based on a number of variables and assumptions that could change over time. The actual savings derived may be higher or lower.
Return to TOP
Return to HOME
|  |  | Existing |  | Total Proposed
| Annual Energy Costs |  | 0 | 0 | 0 |  |  |  | 0
| Annual Energy Savings |  | Proposed (1) |  | Proposed (2) | Proposed (3)
|  |  | 0 |  | 0 | 0
| 0% |  | Please Select | [6 empty] | Year One | Year Two | Year Three | Year Four | Year Five | NPV | NPV Index
| 10% |  | 0% |  |  |  |  | Discount |  | #N/A | #N/A | #N/A | #N/A | #N/A
| 20% |  | 1% |  |  |  |  | 0
| 30% |  | 2% |  |  |  |  | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 40% |  | 3%
| 50% |  | 4%
| 60% |  | 5%
| 70% |  | 6%
| 80% |  | 7%
| 90% |  | 8%
| 100% |  | 9%
10%
11%
12%
13%
14%
15%
Note on C19: If there are controls on the system enter the quantity of luminaires equipped with the controls. If there are no controls, field should have a zero.
Note on C20: The amount of time the fixture are controlled - meaning the percentage of time the fixture are off or dimmed.
Note on C21: Enter the percent of light output of the luminaires that will be controlled. The balance (%) represents the light output of the luminaires when controls are active.

## Energy Analysis
Insert Logo Here
Lighting System Energy Analysis
Input
Output
Customer Information |  |  | Facility Information
Project Name:
Cost Per kWh
Contact: |  |  | Annual Operating Hrs
System Information |  | Existing |  | Proposed
Luminaire Description
Input Watts Per Luminaire
Quantity
| System Watts | 0 |  | 0
| System kW | 0 |  | 0
| Annual kWh | 0 |  | 0
| Annual Energy Costs | 0 |  | 0
| Monthly Costs | 0 |  | 0
| Annual Energy Savings ($) |  |  | 0
| Annual Energy Savings (%) |  |  | #DIV/0!
| Cost of Waiting (Monthly) |  |  | 0
Note: These are estimated savings only. These annual and monthly savings are based on a number of variables and assumptions that could change over time. The actual savings derived by your firm may be higher or lower.
Return to TOP
|  | Existing | Proposed
Return to HOME |  | 0 | 0
Annual Energy Savings

## Opportunity Estimator
Insert Logo Here |  |  | Retrofit Opportunity Estimator
Input |  |  | Identifies the Energy Savings Potential of a Retrofit Opportunity from Annual Lamp Sales.
Output
Customer Information | [5 empty] | Facility Information
Project Name:
Annual Operating Hours
Contact: | [5 empty] | Cost per kWh
Lamp Sales Opportunity |  |  |  |  | System 1 | System 2 | System 3
Number of Lamps Sold Annualized
|  |  | Description of Lamp |  | Please Select | Please Select | Please Select
Lamp Life
Nominal Fixture Wattage
Estimated Number of Fixtures
Total Wattage
Annual Energy Cost
|  |  | (%) Estimated Savings |  | Please Select | Please Select | Please Select
|  |  | ($) Estimated Savings |  | 0 | 0 | 0
|  |  | Total Estimated Savings ($) |  |  |  | 0
Try a fluorescent solution from Cooper Lighting with our We Light You sample demonstration program. Cooper Lighting allows up to 90 days delayed billing from acceptance of delivery to measure the visible and energy saving results of up to six stock luminaires.
Note: These are estimated savings only based on a number of variables, assumptions, and estimated system wattage. The actual energy consumption and savings derived may be higher or lower.
Cooper Lighting • energysolutions@cooperindustries.com • (P) 770-486-4800 • www.cooperenergysolutions.com
Return to HOME
Please Select
20%
25%
30%
| Please Select |  |  |  |  | 35%
| HID, 150W HPS | 188 | 24000 |  |  | 40%
| HID, 250W HPS | 300 | 24000 |  |  | 45%
| HID, 400W HPS | 464 | 24000 |  |  | 50%
| HID, 1000W HPS | 1100 | 24000
| HID, 175W MH | 213 | 10000
| HID, 250W MH | 295 | 10000
| HID, 400W MH | 455 | 20000
| HID, 1000W MH | 1085 | 15000
| HID, 150W PSMH | 189 | 15000
| HID, 175W PSMH | 208 | 15000
| HID, 250W PSMH | 291 | 15000
| HID, 320W PSMH | 368 | 20000
| HID, 350W PSMH | 400 | 20000
| HID, 400W PSMH | 404 | 20000
| HID, 750W PSMH | 820 | 16000
| HID, 1000W PSMH | 1080 | 12000
| HID, 70W ECON PSMH | 80 | 15000
| HID, 100W ECON PSMH | 110 | 10000
| HID, 150W ECON PSMH | 189 | 12000
| HID, 175W ECON PSMH | 194 | 15000
| HID, 250W ECON PSMH | 269 | 15000
| HID, 320W ECON PSMH | 345 | 30000
| HID, 350W ECON PSMH | 375 | 30000
| HID, 400W ECON PSMH | 426 | 30000
| Fluorescent, 34W T12 | 50 | 20000
| Fluorescent, 40W T12 | 57 | 20000
| Fluorescent, 60W T12 SL | 78 | 12000
| Fluorescent, 95W T12 HO | 125 | 12000
| Fluorescent, 110W T12 HO | 145 | 12000
| Fluorescent, 34W T12 U Lamp | 60 | 14000
| Fluorescent, 40W T12 U Lamp | 70 | 14000
| Fluorescent, 215W T12 VHO | 216 | 9000
| Fluorescent, 28W T5 | 34 | 30000
| Fluorescent, 54W T5 HO | 62 | 30000
| Fluorescent, 32W T8 | 28 | 20000
| Fluorsecent, 32W T8 Extra Life | 28 | 30000
| Fluorescent, 32W T8 U Lamp | 35 | 20000
| Compact Fluorescent, PL-H |  | 20000
| Compact Fluorescent, Double/Triple Biax |  | 12000
Note on E19: Based on generic system wattages. Consult lamp and ballast manufacturer's catalog data for precise values.
Note on E20: Value is based on rated lamp life, derived from lamp manufacturer's catalogs, and annual operating hours. Assumes spot relamping.

## Cost of Waiting
Insert Logo Here
Cost of Waiting
Input
Output
Customer Information |  |  | Facility Information
Project Name:
Annual Operating Hrs
Contact: |  |  | Cost Per kWh
System Information |  | Existing |  | Proposed
Luminaire Description
Input Watts Per Luminaire
Quantity
| System Watts | 0 |  | 0
| Luminaire kW | 0 |  | 0
| Annual kWh | 0 |  | 0
| Annual Energy Costs | 0 |  | 0
| Monthly Costs | 0 |  | 0
| Annual Cost of Waiting | 0
| Monthly Cost of Waiting | 0
Note: These are estimated savings only. These annual and monthly savings are based on a number of variables and assumptions that could change over time. The actual savings derived by your firm may be higher or lower.
Return to HOME

## LPD EZ-EPAct
Insert Logo Here
Determining Lighting Power Density (LPD) ASHRAE 90.1 2001
Input
Output
Customer Information |  |  | Facility Information
Project Name:
Area Square Footage
Contact:
Lighting System Details |  | System 1 |  | System 2
Number of Luminaires
System Watts
| Total System Load (kW) | 0 |  | 0
| Watts Per Sq. Ft. | #DIV/0! |  | #DIV/0!
| Percentage Reduction |  |  | #DIV/0!
Compared to ASHRAE 90.1-2001 (The standard for EPAct)
| Application | Manufacturing Facility
| Building Area Method (w/sq ft) | 2.2
| Watts/sq ft versus EPAct | #DIV/0! |  | #DIV/0!
| Potential Per Square Foot Savings |  |  | #DIV/0!
| Total Potential EPAct (Pre-Tax) Deduction Benefit |  |  | #DIV/0!
| Federal Tax Rate | 35%
Per Luminaire Cost
| Lot Labor, Recycle, Disposal Costs |  |  | 0
| Total Installed Cost |  |  | 0
| After Tax EPAct Deduction Benefit |  |  | #DIV/0!
This spreadsheet is meant to provide a generic estimation of the interim tax provisions of the Energy Policy Act of 2005. Please contact your tax advisor to determine the specific tax treatement appropriate for your company.
Return to TOP
Return to HOME
| ASHRAE 90.1 Building Area Method Lighting Power Densities |  |  | 0.3 | 0.32 | 0.34 | 0.36 | 0.38 | 0.4 | 0.42 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56 | 0.58 | 0.6
|  | 2001 |  | 25% | 26% | 27% | 28% | 29% | 30% | 31% | 32% | 33% | 34% | 35% | 36% | 37% | 38% | 39% | 40%
| Automotive Facility | 1.5 |  | 1.125 | 1.11 | 1.095 | 1.08 | 1.065 | 1.05 | 1.035 | 1.02 | 1.005 | 0.99 | 0.975 | 0.96 | 0.945 | 0.93 | 0.915 | 0.6
| Convention Center | 1.4 |  | 1.05 | 1.036 | 1.022 | 1.008 | 0.994 | 0.98 | 0.966 | 0.952 | 0.938 | 0.924 | 0.91 | 0.896 | 0.882 | 0.868 | 0.854 | 0.56
| Court House | 1.4 |  | 1.05 | 1.036 | 1.022 | 1.008 | 0.994 | 0.98 | 0.966 | 0.952 | 0.938 | 0.924 | 0.91 | 0.896 | 0.882 | 0.868 | 0.854 | 0.56
| Dining: Bar, Lounge, Leisure | 1.5 |  | 1.125 | 1.11 | 1.095 | 1.08 | 1.065 | 1.05 | 1.035 | 1.02 | 1.005 | 0.99 | 0.975 | 0.96 | 0.945 | 0.93 | 0.915 | 0.6
| Dining: Cafeteria, Fast Food | 1.8 |  | 1.35 | 1.332 | 1.314 | 1.296 | 1.278 | 1.26 | 1.242 | 1.224 | 1.206 | 1.188 | 1.17 | 1.152 | 1.134 | 1.116 | 1.098 | 0.72
| Dining: Family | 1.9 |  | 1.425 | 1.406 | 1.387 | 1.368 | 1.349 | 1.33 | 1.311 | 1.292 | 1.273 | 1.254 | 1.235 | 1.216 | 1.197 | 1.178 | 1.159 | 0.76
| Dormitory | 1.5 |  | 1.125 | 1.11 | 1.095 | 1.08 | 1.065 | 1.05 | 1.035 | 1.02 | 1.005 | 0.99 | 0.975 | 0.96 | 0.945 | 0.93 | 0.915 | 0.6
| Exercise Center | 1.4 |  | 1.05 | 1.036 | 1.022 | 1.008 | 0.994 | 0.98 | 0.966 | 0.952 | 0.938 | 0.924 | 0.91 | 0.896 | 0.882 | 0.868 | 0.854 | 0.56
| Gymnasium | 1.7 |  | 1.275 | 1.258 | 1.241 | 1.224 | 1.207 | 1.19 | 1.173 | 1.156 | 1.139 | 1.122 | 1.105 | 1.088 | 1.071 | 1.054 | 1.037 | 0.68
| Healthcare Clinic | 1.6 |  | 1.2 | 1.184 | 1.168 | 1.152 | 1.136 | 1.12 | 1.104 | 1.088 | 1.072 | 1.056 | 1.04 | 1.024 | 1.008 | 0.992 | 0.976 | 0.64
| Hospital | 1.6 |  | 1.2 | 1.184 | 1.168 | 1.152 | 1.136 | 1.12 | 1.104 | 1.088 | 1.072 | 1.056 | 1.04 | 1.024 | 1.008 | 0.992 | 0.976 | 0.64
| Hotel | 1.7 |  | 1.275 | 1.258 | 1.241 | 1.224 | 1.207 | 1.19 | 1.173 | 1.156 | 1.139 | 1.122 | 1.105 | 1.088 | 1.071 | 1.054 | 1.037 | 0.68
| Library | 1.5 |  | 1.125 | 1.11 | 1.095 | 1.08 | 1.065 | 1.05 | 1.035 | 1.02 | 1.005 | 0.99 | 0.975 | 0.96 | 0.945 | 0.93 | 0.915 | 0.6
| Manufacturing Facility | 2.2 |  | 1.65 | 1.628 | 1.606 | 1.584 | 1.562 | 1.54 | 1.518 | 1.496 | 1.474 | 1.452 | 1.43 | 1.408 | 1.386 | 1.364 | 1.342 | 0.88
| Motel | 2 |  | 1.5 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.38 | 1.36 | 1.34 | 1.32 | 1.3 | 1.28 | 1.26 | 1.24 | 1.22 | 0.8
| Motion Picture Theater | 1.6 |  | 1.2 | 1.184 | 1.168 | 1.152 | 1.136 | 1.12 | 1.104 | 1.088 | 1.072 | 1.056 | 1.04 | 1.024 | 1.008 | 0.992 | 0.976 | 0.64
| Multi-Family | 1 |  | 0.75 | 0.74 | 0.73 | 0.72 | 0.71 | 0.7 | 0.69 | 0.68 | 0.67 | 0.66 | 0.65 | 0.64 | 0.63 | 0.62 | 0.61 | 0.4
| Museum | 1.6 |  | 1.2 | 1.184 | 1.168 | 1.152 | 1.136 | 1.12 | 1.104 | 1.088 | 1.072 | 1.056 | 1.04 | 1.024 | 1.008 | 0.992 | 0.976 | 0.64
| Office | 1.3 |  | 0.975 | 0.962 | 0.949 | 0.936 | 0.923 | 0.91 | 0.897 | 0.884 | 0.871 | 0.858 | 0.845 | 0.832 | 0.819 | 0.806 | 0.793 | 0.52
| Parking Garage | 0.3 |  | 0.225 | 0.222 | 0.219 | 0.216 | 0.213 | 0.21 | 0.207 | 0.204 | 0.201 | 0.198 | 0.195 | 0.192 | 0.189 | 0.186 | 0.183 | 0.12
| Penitentiary | 1.2 |  | 0.9 | 0.888 | 0.876 | 0.864 | 0.852 | 0.84 | 0.828 | 0.816 | 0.804 | 0.792 | 0.78 | 0.768 | 0.756 | 0.744 | 0.732 | 0.48
| Performing Arts Theatre | 1.5 |  | 1.125 | 1.11 | 1.095 | 1.08 | 1.065 | 1.05 | 1.035 | 1.02 | 1.005 | 0.99 | 0.975 | 0.96 | 0.945 | 0.93 | 0.915 | 0.6
| Police/Fire Station | 1.3 |  | 0.975 | 0.962 | 0.949 | 0.936 | 0.923 | 0.91 | 0.897 | 0.884 | 0.871 | 0.858 | 0.845 | 0.832 | 0.819 | 0.806 | 0.793 | 0.52
| Post Office | 1.6 |  | 1.2 | 1.184 | 1.168 | 1.152 | 1.136 | 1.12 | 1.104 | 1.088 | 1.072 | 1.056 | 1.04 | 1.024 | 1.008 | 0.992 | 0.976 | 0.64
| Religious Building | 2.2 |  | 1.65 | 1.628 | 1.606 | 1.584 | 1.562 | 1.54 | 1.518 | 1.496 | 1.474 | 1.452 | 1.43 | 1.408 | 1.386 | 1.364 | 1.342 | 0.88
| Retail | 1.9 |  | 1.425 | 1.406 | 1.387 | 1.368 | 1.349 | 1.33 | 1.311 | 1.292 | 1.273 | 1.254 | 1.235 | 1.216 | 1.197 | 1.178 | 1.159 | 0.76
| School, University | 1.5 |  | 1.125 | 1.11 | 1.095 | 1.08 | 1.065 | 1.05 | 1.035 | 1.02 | 1.005 | 0.99 | 0.975 | 0.96 | 0.945 | 0.93 | 0.915 | 0.6
| Sports Arena | 1.5 |  | 1.125 | 1.11 | 1.095 | 1.08 | 1.065 | 1.05 | 1.035 | 1.02 | 1.005 | 0.99 | 0.975 | 0.96 | 0.945 | 0.93 | 0.915 | 0.6
| Town Hall | 1.4 |  | 1.05 | 1.036 | 1.022 | 1.008 | 0.994 | 0.98 | 0.966 | 0.952 | 0.938 | 0.924 | 0.91 | 0.896 | 0.882 | 0.868 | 0.854 | 0.56
| Transportation | 1.2 |  | 0.9 | 0.888 | 0.876 | 0.864 | 0.852 | 0.84 | 0.828 | 0.816 | 0.804 | 0.792 | 0.78 | 0.768 | 0.756 | 0.744 | 0.732 | 0.48
| Warehouse | 1.2 |  | 25%: 0.6
| Workshop | 1.7 |  | 1.275 | 1.258 | 1.241 | 1.224 | 1.207 | 1.19 | 1.173 | 1.156 | 1.139 | 1.122 | 1.105 | 1.088 | 1.071 | 1.054 | 1.037 | 0.68
25% | 0.3
26% | 0.32
27% | 0.34
28% | 0.36
29% | 0.38
30% | 0.4
31% | 0.42
32% | 0.44
33% | 0.46
34% | 0.48
35% | 0.5
36% | 0.52
37% | 0.54
38% | 0.56
39% | 0.58
40% | 0.6
41% | 0.6
42% | 0.6
43% | 0.6
44% | 0.6
45% | 0.6
46% | 0.6
47% | 0.6
48% | 0.6
49% | 0.6
50% | 0.6
51% | 0.6
52% | 0.6
53% | 0.6
54% | 0.6
55% | 0.6
56% | 0.6
57% | 0.6
58% | 0.6
59% | 0.6
60% | 0.6
61% | 0.6
62% | 0.6
63% | 0.6
64% | 0.6
65% | 0.6
66% | 0.6
67% | 0.6
68% | 0.6
69% | 0.6
70% | 0.6
71% | 0.6
72% | 0.6
73% | 0.6
74% | 0.6
75% | 0.6
76% | 0.6
77% | 0.6
78% | 0.6
79% | 0.6
80% | 0.6
81% | 0.6
82% | 0.6
83% | 0.6
84% | 0.6
85% | 0.6
86% | 0.6
87% | 0.6
88% | 0.6
89% | 0.6
90% | 0.6
91% | 0.6
92% | 0.6
93% | 0.6
94% | 0.6
95% | 0.6
96% | 0.6
97% | 0.6
98% | 0.6
99% | 0.6
Note on C35: EPAct allows for the accelerated deduction of the lesser of the cost of the project or the value of the savings based on the Interims sliding scale rule. This value is then multiplied by the federal tax rate to determine the actual value of the accelerated deduction. For more information on EPAct please see the recommended links in the Website Links tab.

## LPD 90.1 2004
Insert Logo Here
Determining Lighting Power Density (LPD) ASHRAE 90.1 2004
Input
Output
Customer Information |  |  | Facility Information
Project Name:
Area Square Footage
Contact:
Lighting System Details |  | System 1 |  | System 2
Number of Luminaires
System Watts
| Total System Load (kW) | 0 |  | 0
| Watts Per Sq. Ft. | #DIV/0! |  | #DIV/0!
| Percentage Reduction |  |  | #DIV/0!
| ASHRAE Application | Automotive Facility
| 90.1 2004 Building Area Method (w/sq ft) | 0.9
| Watts/sq ft versus 2004 Code | #DIV/0! |  | #DIV/0!
This spreadsheet is meant to provide a generic estimation. Please contact a LEED-AP to determine the specific requirements to achieve LEED recognition.
Return to TOP
Return to HOME
| ASHRAE 90.1 Building Area Method Lighting Power Densities |  |  | 0.3 | 0.32 | 0.34 | 0.36 | 0.38 | 0.4 | 0.42 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56 | 0.58 | 0.6
|  | 2004 |  | 25% | 26% | 27% | 28% | 29% | 30% | 31% | 32% | 33% | 34% | 35% | 36% | 37% | 38% | 39% | 40%
| Automotive Facility | 0.9 |  | 0.675 | 0.666 | 0.657 | 0.648 | 0.639 | 0.63 | 0.621 | 0.612 | 0.603 | 0.594 | 0.585 | 0.576 | 0.567 | 0.558 | 0.549 | 0.36
| Convention Center | 1.2 |  | 0.9 | 0.888 | 0.876 | 0.864 | 0.852 | 0.84 | 0.828 | 0.816 | 0.804 | 0.792 | 0.78 | 0.768 | 0.756 | 0.744 | 0.732 | 0.48
| Court House | 1.2 |  | 0.9 | 0.888 | 0.876 | 0.864 | 0.852 | 0.84 | 0.828 | 0.816 | 0.804 | 0.792 | 0.78 | 0.768 | 0.756 | 0.744 | 0.732 | 0.48
| Dining: Bar, Lounge, Leisure | 1.3 |  | 0.975 | 0.962 | 0.949 | 0.936 | 0.923 | 0.91 | 0.897 | 0.884 | 0.871 | 0.858 | 0.845 | 0.832 | 0.819 | 0.806 | 0.793 | 0.52
| Dining: Cafeteria, Fast Food | 1.4 |  | 1.05 | 1.036 | 1.022 | 1.008 | 0.994 | 0.98 | 0.966 | 0.952 | 0.938 | 0.924 | 0.91 | 0.896 | 0.882 | 0.868 | 0.854 | 0.56
| Dining: Family | 1.6 |  | 1.2 | 1.184 | 1.168 | 1.152 | 1.136 | 1.12 | 1.104 | 1.088 | 1.072 | 1.056 | 1.04 | 1.024 | 1.008 | 0.992 | 0.976 | 0.64
| Dormitory | 1 |  | 0.75 | 0.74 | 0.73 | 0.72 | 0.71 | 0.7 | 0.69 | 0.68 | 0.67 | 0.66 | 0.65 | 0.64 | 0.63 | 0.62 | 0.61 | 0.4
| Exercise Center | 1 |  | 0.75 | 0.74 | 0.73 | 0.72 | 0.71 | 0.7 | 0.69 | 0.68 | 0.67 | 0.66 | 0.65 | 0.64 | 0.63 | 0.62 | 0.61 | 0.4
| Gymnasium | 1.1 |  | 0.825 | 0.814 | 0.803 | 0.792 | 0.781 | 0.77 | 0.759 | 0.748 | 0.737 | 0.726 | 0.715 | 0.704 | 0.693 | 0.682 | 0.671 | 0.44
| Healthcare Clinic | 1 |  | 0.75 | 0.74 | 0.73 | 0.72 | 0.71 | 0.7 | 0.69 | 0.68 | 0.67 | 0.66 | 0.65 | 0.64 | 0.63 | 0.62 | 0.61 | 0.4
| Hospital | 1.2 |  | 0.9 | 0.888 | 0.876 | 0.864 | 0.852 | 0.84 | 0.828 | 0.816 | 0.804 | 0.792 | 0.78 | 0.768 | 0.756 | 0.744 | 0.732 | 0.48
| Hotel | 1 |  | 0.75 | 0.74 | 0.73 | 0.72 | 0.71 | 0.7 | 0.69 | 0.68 | 0.67 | 0.66 | 0.65 | 0.64 | 0.63 | 0.62 | 0.61 | 0.4
| Library | 1.3 |  | 0.975 | 0.962 | 0.949 | 0.936 | 0.923 | 0.91 | 0.897 | 0.884 | 0.871 | 0.858 | 0.845 | 0.832 | 0.819 | 0.806 | 0.793 | 0.52
| Manufacturing Facility | 1.3 |  | 0.975 | 0.962 | 0.949 | 0.936 | 0.923 | 0.91 | 0.897 | 0.884 | 0.871 | 0.858 | 0.845 | 0.832 | 0.819 | 0.806 | 0.793 | 0.52
| Motel | 1 |  | 0.75 | 0.74 | 0.73 | 0.72 | 0.71 | 0.7 | 0.69 | 0.68 | 0.67 | 0.66 | 0.65 | 0.64 | 0.63 | 0.62 | 0.61 | 0.4
| Motion Picture Theater | 1.2 |  | 0.9 | 0.888 | 0.876 | 0.864 | 0.852 | 0.84 | 0.828 | 0.816 | 0.804 | 0.792 | 0.78 | 0.768 | 0.756 | 0.744 | 0.732 | 0.48
| Multi-Family | 0.7 |  | 0.525 | 0.518 | 0.511 | 0.504 | 0.497 | 0.49 | 0.483 | 0.476 | 0.469 | 0.462 | 0.455 | 0.448 | 0.441 | 0.434 | 0.427 | 0.28
| Museum | 1.1 |  | 0.825 | 0.814 | 0.803 | 0.792 | 0.781 | 0.77 | 0.759 | 0.748 | 0.737 | 0.726 | 0.715 | 0.704 | 0.693 | 0.682 | 0.671 | 0.44
| Office | 1 |  | 0.75 | 0.74 | 0.73 | 0.72 | 0.71 | 0.7 | 0.69 | 0.68 | 0.67 | 0.66 | 0.65 | 0.64 | 0.63 | 0.62 | 0.61 | 0.4
| Parking Garage | 0.3 |  | 0.225 | 0.222 | 0.219 | 0.216 | 0.213 | 0.21 | 0.207 | 0.204 | 0.201 | 0.198 | 0.195 | 0.192 | 0.189 | 0.186 | 0.183 | 0.12
| Penitentiary | 1 |  | 0.75 | 0.74 | 0.73 | 0.72 | 0.71 | 0.7 | 0.69 | 0.68 | 0.67 | 0.66 | 0.65 | 0.64 | 0.63 | 0.62 | 0.61 | 0.4
| Performing Arts Theatre | 1.6 |  | 1.2 | 1.184 | 1.168 | 1.152 | 1.136 | 1.12 | 1.104 | 1.088 | 1.072 | 1.056 | 1.04 | 1.024 | 1.008 | 0.992 | 0.976 | 0.64
| Police/Fire Station | 1 |  | 0.75 | 0.74 | 0.73 | 0.72 | 0.71 | 0.7 | 0.69 | 0.68 | 0.67 | 0.66 | 0.65 | 0.64 | 0.63 | 0.62 | 0.61 | 0.4
| Post Office | 1.1 |  | 0.825 | 0.814 | 0.803 | 0.792 | 0.781 | 0.77 | 0.759 | 0.748 | 0.737 | 0.726 | 0.715 | 0.704 | 0.693 | 0.682 | 0.671 | 0.44
| Religious Building | 1.3 |  | 0.975 | 0.962 | 0.949 | 0.936 | 0.923 | 0.91 | 0.897 | 0.884 | 0.871 | 0.858 | 0.845 | 0.832 | 0.819 | 0.806 | 0.793 | 0.52
| Retail | 1.5 |  | 1.125 | 1.11 | 1.095 | 1.08 | 1.065 | 1.05 | 1.035 | 1.02 | 1.005 | 0.99 | 0.975 | 0.96 | 0.945 | 0.93 | 0.915 | 0.6
| School, University | 1.2 |  | 0.9 | 0.888 | 0.876 | 0.864 | 0.852 | 0.84 | 0.828 | 0.816 | 0.804 | 0.792 | 0.78 | 0.768 | 0.756 | 0.744 | 0.732 | 0.48
| Sports Arena | 1.1 |  | 0.825 | 0.814 | 0.803 | 0.792 | 0.781 | 0.77 | 0.759 | 0.748 | 0.737 | 0.726 | 0.715 | 0.704 | 0.693 | 0.682 | 0.671 | 0.44
| Town Hall | 1.1 |  | 0.825 | 0.814 | 0.803 | 0.792 | 0.781 | 0.77 | 0.759 | 0.748 | 0.737 | 0.726 | 0.715 | 0.704 | 0.693 | 0.682 | 0.671 | 0.44
| Transportation | 1 |  | 0.75 | 0.74 | 0.73 | 0.72 | 0.71 | 0.7 | 0.69 | 0.68 | 0.67 | 0.66 | 0.65 | 0.64 | 0.63 | 0.62 | 0.61 | 0.4
| Warehouse | 0.8 |  | 25%: 0.6
| Workshop | 1.4 |  | 1.05 | 1.036 | 1.022 | 1.008 | 0.994 | 0.98 | 0.966 | 0.952 | 0.938 | 0.924 | 0.91 | 0.896 | 0.882 | 0.868 | 0.854 | 0.56
25% | 0.3
26% | 0.32
27% | 0.34
28% | 0.36
29% | 0.38
30% | 0.4
31% | 0.42
32% | 0.44
33% | 0.46
34% | 0.48
35% | 0.5
36% | 0.52
37% | 0.54
38% | 0.56
39% | 0.58
40% | 0.6
41% | 0.6
42% | 0.6
43% | 0.6
44% | 0.6
45% | 0.6
46% | 0.6
47% | 0.6
48% | 0.6
49% | 0.6
50% | 0.6
51% | 0.6
52% | 0.6
53% | 0.6
54% | 0.6
55% | 0.6
56% | 0.6
57% | 0.6
58% | 0.6
59% | 0.6
60% | 0.6
61% | 0.6
62% | 0.6
63% | 0.6
64% | 0.6
65% | 0.6
66% | 0.6
67% | 0.6
68% | 0.6
69% | 0.6
70% | 0.6
71% | 0.6
72% | 0.6
73% | 0.6
74% | 0.6
75% | 0.6
76% | 0.6
77% | 0.6
78% | 0.6
79% | 0.6
80% | 0.6
81% | 0.6
82% | 0.6
83% | 0.6
84% | 0.6
85% | 0.6
86% | 0.6
87% | 0.6
88% | 0.6
89% | 0.6
90% | 0.6
91% | 0.6
92% | 0.6
93% | 0.6
94% | 0.6
95% | 0.6
96% | 0.6
97% | 0.6
98% | 0.6
99% | 0.6

## EPAct Certification
TAX DEDUCTION FOR ENERGY EFFICIENT COMMERCIAL BUILDINGS
ENERGY POLICY ACT OF 2005, ENACTED SECTION 179D
CERTIFICATE OF COMPLIANCE
| Certified By: |  |  |  |  | Date:
Name:
Company:
Street Address:
|  | City: |  |  |  | State:
|  | Zip Code: |  | Telephone:
Building Certified:
Street Address:
|  | City: |  |  |  | State:
Zip Code:
|  | Energy efficient system installed and placed in service during: |  |  | CY2006 | CY2007 | CY2008
Certification Statement (per Notice 2006-52): (Check One)
Statement for energy efficient commercial building property:
“The interior lighting systems, heating, cooling, ventilation and hot water systems, and building envelope that have been, or are planned to be, incorporated into the building will reduce the total annual energy and power costs with respect to combined usage of the building’s heating, cooling, ventilation, hot water, and interior lighting systems by 50 percent or more as compared to a Reference Building that meets the minimum requirements of Standard 90.1-2001.”
Statement for energy efficient lighting property that satisfies the requirements of the permanent rule of section 2.03(1)(a) of this notice:
“The interior lighting systems that have been, or are planned to be, incorporated into the building will reduce the total annual energy and power costs with respect to combined usage of the building’s heating, cooling, ventilation, hot water, and interior lighting systems by 16 2/3 percent or more as compared to a Reference Building that meets the minimum requirements of Standard 90.1-2001.”
Statement for energy efficient lighting property that satisfied the requirements of the interim rule of section 2.03(1)(b) of this notice:
“The interior lighting systems that have been, or are planned to be, incorporated into the building satisfy the requirements of the interim rule of section 2.03(1)(b) of this notice. The interior lighting systems that have been, or are planned to be, incorporated into the building satisfy the requirements of the interim rule of section 2.03(1)(b) of Notice 2006-52.”
I hereby certify the following:
| 1.) | Field inspections of the building, performed by a qualified individual after the property has been placed in service, have confirmed that the building has met, or will meet, the energy-saving targets contained in the design plans and specifications, and that the field inspections were performed in accordance with any inspection and testing procedures that (1) have been prescribed by the National Renewable Energy Laboratory (NREL) as Energy Savings Modeling and Inspection Guidelines for Commercial Building Federal Tax Deductions and (2) are in effect at the time the certification is given.
| 2.) | The building owner has received an explanation of the energy efficiency features of the building and its projected annual energy costs.
| 3.) | Qualified computer software was used to calculate energy and power consumption and costs and identification of the qualified computer software used. (Permanent Rule only)
| 4.) | The attached list identifies the components of the interior lighting systems, heating, cooling, ventilation, and hot water systems, and building envelope installed on or in the building, the energy efficiency features of the building, and its projected annual energy costs.
“Under penalties of perjury, I declare that I have examined this certification, including accompanying documents, including accompanying documents, and to the best of my knowledge and belief, the facts presented in support of this certification are true, correct, and complete.”
Printed Name of Certifier:
|  |  | Signature: |  |  | Date:
|  |  | Check One: | Professional Engineer |  | Licensed Contractor
|  |  |  | PE ID Number |  | License Number:
TAX DEDUCTION FOR ENERGY EFFICIENT COMMERCIAL BUILDINGS
ENERGY POLICY ACT OF 2005, ENACTED SECTION 179D
ATTACHMENT WHEN USING INTERIM LIGHTING RULES
| Certified By: |  |  |  |  | Date:
Name:
Company:
Street Address:
|  | City: |  |  |  | State:
|  | Zip Code: |  | Telephone:
Building Certified:
Street Address:
|  | City: |  |  |  | State:
Zip Code:
|  | Energy efficient system installed and placed in service during: |  |  | CY2006 | CY2007 | CY2008
Statement of Computer Software
The interim lighting rules require a calculation of lighting power density (total connected lighting watts divided by building area), but does not require the calculation of energy and power consumption and costs for the entire building.
Statement of Energy Reduction
|  | Building or Space by Space | Building Area Description | ASHRAE 90.1 2001 LPD (w/sq ft) | Resulting LPD (w/sq ft) | % Below ASHRAE 90.1 | Square Footage
Statement on Components List
[6 empty] | Captialized equipment cost incurred for the energy efficient property | $
[6 empty] | Captialized labor cost incurred for the energy efficient property | $
List components of energy efficient system installed in or on the building:
Statement of Projected Annual Energy Costs:
Statement of Energy Efficient Features
Return to TOP
Return to HOME

## Environmental Impact
Insert Logo Here
Environmental Impact
Input
Output
Customer Information |  |  |  |  | Facility Information
Project Name:
Annual Operating Hours
Contact: |  |  | Cost Per kWh
Lighting System Details |  |  |  | Existing |  | Proposed
Number of Luminaires |  |  | Input Watts Per Luminaire
|  |  | System kW | 0 |  | 0
|  |  | kW Saved |  |  | 0
|  |  | kWh Saved |  |  | 0
Equivalent Environmental Impact*
CO2 Emissions (lbs) |  | 0 | Fewer Cars on the Road |  |  | 0
(tons) |  | 0 | Acres of Trees Planted |  |  | 0
Coal Emissions (lbs) |  | 0 | Equivalent to Annual Electricity Usage of Households (#) |  |  | 0
| (tons) | 0
*Based on Environmental Protection Agency (EPA) emissions factor assumptions.
Return to HOME

## SP Ratio
Insert Logo Here
Scotopic/Photopic Impact
Input
Output
Customer Information
Project Name: |  |  |  | Contact:
Lamp Detail
| Lamp Type | 400W MH |  | S/P Ratio Adjustments
|  |  |  | Brightness | 44090.8154 | Lmns
| S/P Ratio | 1.5 |  | Paper Reading | 49391.6669 | Lmns
| Initial Lumens | 36000 |  | Computer Tasks | 54000 | Lmns
|  | Lamp Type | S/P Ratio (Typical) | Initial Lumens | Mean Lumens
Please Select
| HID | 400W HPS | 0.62 | 51000 | 45000
|  | 400W MH | 1.5 | 36000 | 23500
|  | 350W PSMH | 1.5 | 36500 | 27000
| T12 FLR | F40T12 WW | 1 | 2950 | 2600
|  | F40T12 CW | 1.5 | 2950 | 2600
|  | F40T12-ES CW | 1.5 | 2750 | 2475
|  | F40T12-ES WW | 1 | 2750 | 2475
| T5HO FLR | F54T5HO 830 | 1.3 | 5000 | 4700
|  | F54T5HO 835 | 1.5 | 5000 | 4700
|  | F54T5HO 841 | 1.7 | 5000 | 4700
|  | F54T5HO 850 | 1.9 | 5000 | 4700
| T8 FLR | F32T8 730 | 1.3 | 2800 | 2576
|  | F32T8 735 | 1.5 | 2800 | 2576
|  | F32T8 741 | 1.8 | 2800 | 2576
|  | F32T8 830 | 1.3 | 2800 | 2576
|  | F32T8 835 | 1.41 | 2800 | 2576
|  | F32T8 841 | 1.62 | 2800 | 2576
|  | F32T8 850 | 1.95 | 2800 | 2576
|  | F32T8 HL 730 | 1.3 | 3100 | 2915
|  | F32T8 HL 735 | 1.5 | 3100 | 2915
|  | F32T8 HL 741 | 1.8 | 3100 | 2915
|  | F32T8 HL 830 | 1.3 | 3100 | 2915
|  | F32T8 HL 835 | 1.41 | 3100 | 2915
|  | F32T8 HL 841 | 1.62 | 3100 | 2915
|  | F32T8 HL 850 | 1.95 | 3100 | 2915
While an increasing number of lighting designers are endorsing this approach, the use of S/P ratios has not yet been endorsed by IES. Cooper Lighting provides this background as reference information only and maintains no formal position on its application.
Return to Top
Return to HOME
Note on D2: Scotopic/photopic ratios have been developed that attempt to replicate a measurement system more akin to how our eyes perceive brightness. The S/P Ratio acts as an adjustment to the existing photopic measurement (stated lamp lumens in lamp manufacturers' catalogs) by multiplying the standard lumens of a source with the S/P ratio or a factor thereof.
Note on F14: S/P Impact for Brightness is calculated by multiplying the initial lumens by the S/P Ratio to the power of 0.5
Note on F15: S/P Impact for Reading Paper is calculated by multiplying the initial lumens by the S/P Ratio to the power of 0.78
Note on F16: S/P Impact for Computer Tasks is calculated by multiplying the initial lumens by the S/P Ratio

## SP Ratio Comparison
Insert Logo Here
System Comparison of Scotopic/Photopic Impact
Input
Output
Customer Information
Project Name: |  |  |  | Contact:
Lighting System Details |  |  |  | Existing | Proposed
Luminaire Description
|  |  | Number of Lamps | Please Select | Please Select
|  |  | Lamp Type | Please Select | Please Select
|  |  | S/P Ratio | #N/A | #N/A
|  |  | Initial Lumens | #N/A | #N/A
|  |  | Mean Lumens | #N/A | #N/A
|  |  | S/P Adjusted | 0.5 | Brightness
|  |  | Adjusted Initial Lumens | #N/A | #N/A
|  |  | Adjusted Mean Lumens | #N/A | #N/A
|  |  | % Increased Visual Acuity of S/P Ratio | #N/A | #N/A
System Comparison of S/P Adjusted Mean Lumens |  |  |  |  | #N/A
While an increasing number of lighting designers are endorsing this approach, the use of S/P ratios has not yet been endorsed by IES. Cooper Lighting provides this background as reference information only and maintains no formal position on its application.
Return to HOME
| Please Select | Nominal Wattage | S/P Ratio (Typical) | Initial Lumens | Mean Lumens |  | Please Select
HID | 400W HPS | 400W | 0.62 | 51000 | 45000 |  | 1
| 400W MH | 400W | 1.5 | 36000 | 23500 |  | 2
| 350W PSMH | 350W | 1.5 | 36500 | 27000 |  | 3
| 320W PSMH Econ | 320W | 1.5 | 30000 | 24000 |  | 4
T12 FLR | F40T12 WW | 40W | 1 | 2950 | 2600 |  | 5
| F40T12 CW | 40W | 1.5 | 2950 | 2600 |  | 6
| F40T12-ES CW | 34W | 1.5 | 2750 | 2475 |  | 8
| F40T12-ES WW | 34W | 1 | 2750 | 2475
T5HO FLR | F54T5HO 830 | 54W | 1.3 | 5000 | 4700
| F54T5HO 835 | 54W | 1.5 | 5000 | 4700 |  | 0 | 0
| F54T5HO 841 | 54W | 1.7 | 5000 | 4700 | Initial Lumens | #N/A | #N/A
| F54T5HO 850 | 54W | 1.9 | 5000 | 4700 | S/P Adjusted Lumens | #N/A | #N/A
T8 FLR | F32T8 730 | 32W | 1.3 | 2800 | 2576
| F32T8 735 | 32W | 1.5 | 2800 | 2576
| F32T8 741 | 32W | 1.8 | 2800 | 2576
| F32T8 830 | 32W | 1.3 | 2800 | 2576
| F32T8 835 | 32W | 1.41 | 2800 | 2576 |  | 0.5 | Brightness
| F32T8 841 | 32W | 1.62 | 2800 | 2576 |  | 0.78 | Reading
| F32T8 850 | 32W | 1.95 | 2800 | 2576 |  | 1 | Computer Tasks
| F32T8 HL 730 | 32W | 1.3 | 3100 | 2915
| F32T8 HL 735 | 32W | 1.5 | 3100 | 2915
| F32T8 HL 741 | 32W | 1.8 | 3100 | 2915
| F32T8 HL 830 | 32W | 1.3 | 3100 | 2915
| F32T8 HL 835 | 32W | 1.41 | 3100 | 2915
| F32T8 HL 841 | 32W | 1.62 | 3100 | 2915
| F32T8 HL 850 | 32W | 1.95 | 3100 | 2915
Note on E2: Scotopic/photopic ratios have been developed that attempt to replicate a measurement system more akin to how our eyes perceive brightness. The S/P Ratio acts as an adjustment to the existing photopic measurement (stated lamp lumens in lamp manufacturers' catalogs) by multiplying the standard lumens of a source with the S/P ratio or a factor thereof.
Note on E23: Brightness = P * (S/P)^0.5 Reading Paper = P * (S/P)^0.78 Computer Tasks = P * (S/P)

## CU Table
Insert Logo Here
Typical Coefficient of Utilization (CU)
In general lighting calculations, the fraction of initial lamp lumens that reach the work plane. CU is a function of luminaire efficiency, room surface reflectances and room shape. Below are general CU values based on two different room surface reflectances. The 80 ceiling, 50 wall and 20 floor is typical for office environments where 50/50/20 is for more industrial applications with darker, less reflectant surfaces.
Typical Dirt Depreciation values helpful in various CU calculations are listed below:
| Environment (Dirtiness) | Light | Medium | Heavy
| Enclosed Luminaires | 0.94 | 0.86 | 0.77
| Enclosed & Filtered | 0.97 | 0.93 | 0.88
| Open & Ventilated | 0.94 | 0.84 | 0.74
Industrial Luminaires
| Luminaire | 80/50/20 | 50/50/20 |  | Luminaire | 80/50/20 | 50/50/20
| 4 Lamp T5HO HB FLR Industrial | 0.98 | 0.9 |  | Aluminum High Bay (HID) | 0.85 | 0.79
| 4 Lamp T8 HB FLR Industrial w/White Optic | 0.85 | 0.78 |  | Aluminum High Bay (1000W HID) | 0.78 | 0.73
| 6 Lamp T8 2HB FLR Industrial | 1.01 | 0.94 |  | Acrylic High Bay (HID) | 0.95 | 0.84
| 6 Lamp T5HO 2HB FLR Industrial | 0.95 | 0.9 |  | Low Bay (HID) | 0.85 | 0.79
| I5 Series (FLR) | 0.93 | 0.88 |  | VertX Aisle High Bay (HID) | 0.89 | 0.83
| 8 Lamp T8 3HBO FLR Industrial | 0.95 | 0.88 |  | Vertimark Series (HID) | 0.85 | 0.75
| 8 Lamp T5HO 3HBO FLR Industrial | 0.96 | 0.89
| 6 Lamp T8 FLR Industrial Grid | 0.87 | 0.81 |  | Industrial Strip (FLR) | 0.88 | 0.79
| 6 Lamp T5HO FLR Industrial Grid | 0.77 | 0.73 |  | Strip (FLR) | 0.86 | 0.75
Commercial Luminaires
| Luminaire | 80/50/20 | 50/50/20 |  | Luminaire | 80/50/20 | 50/50/20
| Accord T8 | 0.83 | 0.78 |  | Troffer (Std A12 Lens) | 0.81 | 0.76
| Accord T5 | 0.93 | 0.87 |  | Parabolic (18 Cell, 3" Semi-Specular Louver) | 0.8 | 0.75
| Ovation | 0.7 | 0.66
Return to TOP
Return to HOME
Note on G26: Administrator: DIM
Note on G27: Administrator: SN

## # Fixtures
Insert Logo Here
Luminaire Count Estimator
Input
Output
Customer Information | [5 empty] | Facility Information
Project Name:
Area Square Footage
Contact:
Lighting System Details
|  | Maintained Illuminance |  |  |  | Lamp Type | Please Select
# Lamps in Luminaire
[6 empty] | Lumens Per Lamp | #N/A
|  | Type of Luminaire | Please Select
|  | Coefficient of Utilization | #N/A |  |  | Lamp Lumen Depreciation | #N/A
[6 empty] | Ballast Factor | #N/A
|  | Number of Luminaires | #N/A
This is only an estimate. Cooper Lighting's online zonal cavity calulators and lighting layout software and services should be used for a final evaluation.
Return to HOME
| Please Select | Lumens Per Lamp | Lamp Lumen Depreciation | Ballast Factor
| 40W T12 | 2950 | 0.88 | 0.9
| 40W T12 ES | 2570 | 0.88 | 0.9
| 32W T8 HL | 3100 | 0.94 | 0.9
| 32W T8 HL & HBF | 3100 | 0.94 | 1.15
| 32W T8 | 2800 | 0.94 | 0.9
| 54W T5HO | 5100 | 0.93 | 1
| 400W MH | 36000 | 0.58 | 1
| 1000W MH | 100280 | 0.58 | 1
| 350W PSMH | 41000 | 0.8 | 1
| 400W HPS | 51000 | 0.81 | 1
| 1000W HPS | 130000 | 0.81 | 1
Typical Coefficient of Utilization (CU)
Reflectances
|  | Please Select | 80/50/20 |  | 50/50/20
|  | Aluminum High Bay (HID) | 0.85 |  | 0.79
|  | Aluminum High Bay (1000W HID) | 0.78 |  | 0.73
|  | Acrylic High Bay (HID) | 0.95 |  | 0.84
|  | Low Bay (HID) | 0.85 |  | 0.79
|  | Fluorescent Industrial (FLR) | 0.88 |  | 0.79
|  | VertX Aisle High Bay (HID) | 0.89 |  | 0.83
|  | Vertimark Series (HID) | 0.85 |  | 0.75
|  | 8 Lamp T5HO 3HBO F-Bay | 0.96 |  | 0.89
|  | 8 Lamp T8 3HBO F-Bay | 0.95 |  | 0.88
|  | I5 Series (FLR) | 0.93 |  | 0.88
|  | 6 Lamp T8 F-Bay Grid | 0.87 |  | 0.81
|  | 6 Lamp T5HO F-Bay Grid | 0.77 |  | 0.73
|  | 4 Lamp T8 2HB F-Bay | 0.96 |  | 0.9
|  | 6 Lamp T8 2HB F-Bay | 1.01 |  | 0.94
|  | 6 Lamp T5HO 2HB F-Bay | 0.95 |  | 0.9
|  | Strip (FLR) | 0.86 |  | 0.75
|  | Troffer (FLR) | 0.81 |  | 0.76
|  | Parabolic (18C 3") | 0.8 |  | 0.75
|  | Accord T8 | 0.83 |  | 0.78
|  | Accord T5 | 0.93 |  | 0.87
|  | Ovation Recessed Direct/Indirect | 0.7 |  | 0.66
Note on D14: Footcandle Requirement based on IESNA recommended light levels
Note on D48: Administrator: DIM
Note on D59: Administrator: SN
Note on D60: Administrator: G
Note on D61: Administrator: 18C

## Common FC
Insert Logo Here | Footcandle Requirements for Common Applications*
Application |  | Horz | Vert | Application | Horz | Vert
Offices |  |  |  | Manufacturing & Warehouse
Open |  | 30 | 5 | Raw Material Processing
Data Processing Tasks |  | 3 | 3 | Coarse | 10
Printed Tasks |  | 30 |  | Medium | 30
Private |  | 50 | 5 | Fine | 50
Lobby, Reception Area |  | 10 | 3 | Very Fine | 100
Conference Rooms |  |  |  | Materials Handling
Meeting |  | 30 | 5 | Wrapping, Packaging And Labeling | 30
Video Conference |  | 50 | 30 | Picking Stock, Classifying | 30
Exhibition Halls |  | 10 | 3 | Component Manufacturing
Stairways & Corridors |  | 5 |  | Large | 30
Toilets & Washrooms |  | 5 |  | Medium | 50
Shopping Mall & Retail |  |  |  | Fine | 100
Main Concourse |  | 30 | 5 | Machining
Service Corridors |  | 30 |  | Assembly
General Retail |  | 50 |  | Simple | 30
Stock Rooms, Wrapping & Packaging |  | 30 |  | Difficult | 100
Supermarkets |  | 50 | 10 | Exacting | 300
Food Service |  |  |  | Warehousing And Storage
Kitchen |  | 50 | 3 | Inactive | 5
Food Courts |  | 30 | 3 | Active: Bulky Items; Large Labels | 10
Dining |  | 10 | 3 | Active: Small Items; Small Labels | 30
Hospitals |  |  |  | Shipping And Receiving | 30
Corridors |  | 10 | 3 | Maintenance | 50
General Waiting Areas |  | 10 | 3 | Exterior
General Nursing Station |  | 30 | 5 | Building Exteriors
Lobby |  | 5 | 3 | Entrances | 5 | 3
Medical Records |  | 50 | 10 | Parking Garage
Stairways |  | 10 | 3 | Basic | 1 | 0.5
Hotels |  |  |  | Ramps
Guest Rooms |  | 10 |  | Day | 2 | 1
Corridors, Stairs |  | 5 |  | Night | 1 | 0.5
Lobby |  | 10 |  | Entrance Areas
Educational Facilities |  |  |  | Day | 50 | 25
Corridors |  |  | 10 | Night | 1 | 0.5
Classroom |  | 50 | 30 | Stairways | 2 | 1
Lecture Halls |  | 100 | 50
Gymnasiums
Basketball |  | 100 | 30
Social Events |  | 5 | 3
This table shows a useful sampling of recommended footcandle values, for more comprehensive requirements please consult the IESNA Lighting Design Guide.
Return to TOP
Return to HOME

## FC
Insert Logo Here
Maintained Illuminance (Footcandle)
Input
Output
Customer Information | [5 empty] | Facility Information
Project Name:
Area Square Footage
Contact:
Lighting System Details
|  | Number of Luminaires |  |  |  | Lamp Type | Please Select
# Lamps in Luminaire
[6 empty] | Lumens Per Lamp | #N/A
|  | Type of Luminaire | Please Select
|  | Coefficient of Utilization | #N/A |  |  | Lamp Lumen Depreciation | #N/A
[6 empty] | Ballast Factor | #N/A
|  | Maintained Illuminance | #N/A
This is only an estimate. Cooper Lighting's online zonal cavity calulators and lighting layout software and services should be used for a final evaluation.
Return to HOME
| Please Select | Lumens Per Lamp | Lamp Lumen Depreciation | Ballast Factor
| 40W T12 | 2950 | 0.88 | 0.9
| 40W T12 ES | 2570 | 0.88 | 0.9
| 32W T8 HL | 3100 | 0.94 | 0.9
| 32W T8 HL & HBF | 3100 | 0.94 | 1.15
| 32W T8 | 2800 | 0.94 | 0.9
| 54W T5HO | 5100 | 0.93 | 1
| 400W MH | 36000 | 0.58 | 1
| 1000W MH | 100280 | 0.58 | 1
| 350W PSMH | 41000 | 0.8 | 1
| 400W HPS | 51000 | 0.81 | 1
| 1000W HPS | 130000 | 0.81 | 1
Typical Coefficient of Utilization (CU)
Reflectances
|  | Please Select | 80/50/20 |  | 50/50/20
|  | Aluminum High Bay (HID) | 0.85 |  | 0.79
|  | Aluminum High Bay (1000W HID) | 0.78 |  | 0.73
|  | Acrylic High Bay (HID) | 0.95 |  | 0.84
|  | Low Bay (HID) | 0.85 |  | 0.79
|  | Fluorescent Industrial (FLR) | 0.88 |  | 0.79
|  | VertX Aisle High Bay (HID) | 0.89 |  | 0.83
|  | Vertimark Series (HID) | 0.85 |  | 0.75
|  | 8 Lamp T5HO 3HBO F-Bay | 0.96 |  | 0.89
|  | 8 Lamp T8 3HBO F-Bay | 0.95 |  | 0.88
|  | I5 Series (FLR) | 0.93 |  | 0.88
|  | 6 Lamp T8 F-Bay Grid | 0.87 |  | 0.81
|  | 6 Lamp T5HO F-Bay Grid | 0.77 |  | 0.73
|  | 4 Lamp T8 2HB F-Bay | 0.96 |  | 0.9
|  | 6 Lamp T8 2HB F-Bay | 1.01 |  | 0.94
|  | 6 Lamp T5HO 2HB F-Bay | 0.95 |  | 0.9
|  | Strip (FLR) | 0.86 |  | 0.75
|  | Troffer (FLR) | 0.81 |  | 0.76
|  | Parabolic (18C 3") | 0.8 |  | 0.75
|  | Accord T8 | 0.83 |  | 0.78
|  | Accord T5 | 0.93 |  | 0.87
|  | Ovation Recessed Direct/Indirect | 0.7 |  | 0.66
Note on D21: Footcandle Requirement based on IESNA recommended light levels
Note on D47: Administrator: DIM
Note on D58: Administrator: SN
Note on D59: Administrator: G
Note on D60: Administrator: 18C

## Maintained FC
Insert Logo Here
Maintained Illumination Comparison Over System Life
Input
Output
| Customer Information | [5 empty] | Facility Information
Project Name:
Square Footage
Contact:
| System Information |  |  |  | Existing |  | Proposed
Luminaire Description
|  |  | Type of Luminaire |  | Please Select |  | Please Select
|  |  | Lamp Type |  | Please Select |  | Please Select
[5 empty] | #N/A |  | #N/A
|  |  | # Lamps |  | Please Select |  | Please Select
|  |  | Lamp Lumens |  | #N/A |  | #N/A
|  |  | Initial System Lumens |  | #N/A |  | #N/A
Luminaire Quantity
| Burned in Hours/Hours Since Last Relamp |  |  |  | 28000
|  |  | Lamp Life |  | #N/A |  | #N/A
|  |  | % Depreciation |  | #N/A |  | 40%
|  |  | Depreciation Factor |  | #N/A |  | #N/A
|  |  | Lamp Lumen Depreciation |  | #N/A |  | #N/A
|  |  | Coefficient of Utilization |  | #N/A |  | #N/A
|  |  | Ballast Factor |  | Ballast Factor |  | Ballast Factor
|  |  | Adjusted System Lumens |  | #N/A |  | #N/A
|  |  | Initial Illuminance (FC) |  | #N/A |  | #N/A
|  |  | Time Adjusted System Lumens |  | #N/A |  | #N/A
|  |  | Maintained Illuminance (FC) |  | #N/A |  | #N/A
|  |  | Change in Light Output (Initial) |  |  |  | #N/A
|  |  | Change in Light Output (Maintained) |  |  |  | #N/A
This is only an estimate. Cooper Lighting's online zonal cavity calulators and lighting layout software and services should be used for a final evaluation.
Return to TOP
Return to HOME
|  | Please Select | Lumens Per Lamp | Lamp Lumen Depreciation | Ballast Factor
|  | 32W T8 | 2800 | 0.94 | 0.9 | T8 Fluorescent
|  | 32W T8 HL | 3100 | 0.94 | 0.9 | T8 Fluorescent
|  | 32W T8 HL & HBF | 3100 | 0.94 | 1.15 | T8 Fluorescent
Please Select
|  | 40W T12 | 2950 | 0.88 | 0.9 | T12 Fluorescent |  | 1
|  | 40W T12 ES | 2570 | 0.88 | 0.9 | T12 Fluorescent |  | 2
|  | 110W T12 HO | 9200 | 0.93 | 0.88 | T12 Fluorescent |  | 3
4
|  | 54W T5HO | 5100 | 0.93 | 1 | T5HO Fluorescent |  | 5
6
|  | 250W HPS | 30000 | 0.81 | 1 | High Pressure Sodium |  | 8
|  | 400W HPS | 51000 | 0.81 | 1 | High Pressure Sodium
|  | 1000W HPS | 130000 | 0.81 | 1 | High Pressure Sodium
|  | 250W MH | 20800 | 0.58 | 1 | Probe Start Metal Halide
|  | 400W MH | 36000 | 0.58 | 1 | Probe Start Metal Halide
|  | 1000W MH | 100280 | 0.58 | 1 | Probe Start Metal Halide
|  | 250W PSMH | 23000 | 0.8 | 1 | Pulse Start Metal Halide
|  | 320W PSMH | 32000 | 0.8 | 1 | Pulse Start Metal Halide
|  | 350W PSMH | 41000 | 0.8 | 1 | Pulse Start Metal Halide
|  | 450W PSMH | 44000 | 0.8 | 1 | Pulse Start Metal Halide
|  | 750W PSMH | 82000 | 0.8 | 1 | Pulse Start Metal Halide
|  | 1000W PSMH | 115000 | 0.8 | 1 | Pulse Start Metal Halide
|  | 250W Elec PSMH | 23000 | 0.9 | 1 | Electronic Pulse Start Metal Halide
|  | 320W Elec PSMH | 30000 | 0.9 | 1 | Electronic Pulse Start Metal Halide
|  | Please Select | Lamp Life
|  | 250W HPS | 24000
|  | 400W HPS | 24000
|  | 1000W HPS | 24000
|  | 175W MH | 10000
|  | 250W MH | 10000
|  | 400W MH | 20000
|  | 1000W MH | 15000
|  | 250W PSMH | 15000
|  | 175W PSMH | 15000
|  | 150W PSMH | 15000
|  | 320W PSMH | 20000
|  | 350W PSMH | 20000
|  | 400W PSMH | 20000
|  | 450W PSMH | 20000
|  | 750W PSMH | 16000
|  | 1000W PSMH | 12000
|  | 70W Elec PSMH | 15000
|  | 100W Elec PSMH | 10000
|  | 150W Elec PSMH | 12000
|  | 200W Elec PSMH | 15000
|  | 250W Elec PSMH | 15000
|  | 175W Elec PSMH | 15000
|  | 320W Elec PSMH | 30000
|  | 350W Elec PSMH | 30000
|  | 400W Elec PSMH | 30000
|  | 450W Elec PSMH | 30000
|  | CMH | 20000
|  | 40W T12 | 20000
|  | 40W T12 ES | 20000
|  | 110W T12 HO | 12000
|  | T12 U Lamp | 14000
|  | T12 VHO | 9000
|  | T5 | 30000
|  | 54W T5HO | 30000
|  | 32W T8 | 20000
|  | 32W T8 HL | 30000
|  | 32W T8 HL & HBF | 30000
|  | T8 U Lamp | 20000
|  | PL-H | 20000
|  | Double/Triple Biax | 12000
Typical Coefficient of Utilization (CU)
Reflectances
|  |  | Please Select | 50/50/20 | 80/50/20
|  |  | Aluminum High Bay (HID) | 0.79 | 0.85
|  |  | Aluminum High Bay (1000W HID) | 0.73 | 0.78
|  |  | Acrylic High Bay (HID) | 0.84 | 0.95
|  |  | Low Bay (HID) | 0.79 | 0.85
|  |  | VertX Aisle High Bay (HID) | 0.83 | 0.89
|  |  | Vertimark Series (HID) | 0.75 | 0.85
|  |  | HB T8 F-Bay | 0.9 | 0.96
|  |  | 2HB T8 F-Bay | 0.94 | 1.01
|  |  | 2HB T5HO F-Bay | 0.9 | 0.95
|  |  | I5 Series (FLR) | 0.85 | 0.88
|  |  | I8 Series (FLR) | 0.78 | 0.85
|  |  | MicroBay (T8) | 0.79 | 0.84
|  |  | MicroBay (T5HO) | 0.83 | 0.88
|  |  | 3HBO T5HO F-Bay | 0.89 | 0.96
|  |  | 3HBO T8 F-Bay | 0.88 | 0.95
|  |  | Grid T8 F-Bay | 0.81 | 0.87
|  |  | Grid T5HO F-Bay | 0.73 | 0.77
|  |  | Industrial (FLR) | 0.79 | 0.88
|  |  | Strip (FLR) | 0.75 | 0.86
|  |  | Troffer (FLR) | 0.76 | 0.81
|  |  | Parabolic (18C 3") | 0.75 | 0.8
|  |  | Accord T8 | 0.78 | 0.83
|  |  | Accord T5 | 0.87 | 0.93
|  |  | Ovation Recessed Direct/Indirect | 0.66 | 0.7
|  |  | System | Percent Output | Combo | Depreciation Factor
|  |  | T8 Fluorescent | 0% | T8 Fluorescent-0 | 100 | 100%
|  |  | T8 Fluorescent | 10% | T8 Fluorescent-0.1 | 98 | 98%
|  |  | T8 Fluorescent | 20% | T8 Fluorescent-0.2 | 96 | 96%
|  |  | T8 Fluorescent | 30% | T8 Fluorescent-0.3 | 95.5 | 95.5%
|  |  | T8 Fluorescent | 40% | T8 Fluorescent-0.4 | 95 | 95%
|  |  | T8 Fluorescent | 50% | T8 Fluorescent-0.5 | 94.5 | 94.5%
|  |  | T8 Fluorescent | 60% | T8 Fluorescent-0.6 | 94 | 94%
|  |  | T8 Fluorescent | 70% | T8 Fluorescent-0.7 | 93.5 | 93.5%
|  |  | T8 Fluorescent | 80% | T8 Fluorescent-0.8 | 93 | 93%
|  |  | T8 Fluorescent | 90% | T8 Fluorescent-0.9 | 92.5 | 92.5%
|  |  | T8 Fluorescent | 100% | T8 Fluorescent-1 | 92 | 92%
|  |  | T5HO Fluorescent | 0% | T5HO Fluorescent-0 | 100 | 100%
|  |  | T5HO Fluorescent | 10% | T5HO Fluorescent-0.1 | 98 | 98%
|  |  | T5HO Fluorescent | 20% | T5HO Fluorescent-0.2 | 96 | 96%
|  |  | T5HO Fluorescent | 30% | T5HO Fluorescent-0.3 | 95 | 95%
|  |  | T5HO Fluorescent | 40% | T5HO Fluorescent-0.4 | 94 | 94%
|  |  | T5HO Fluorescent | 50% | T5HO Fluorescent-0.5 | 93 | 93%
|  |  | T5HO Fluorescent | 60% | T5HO Fluorescent-0.6 | 92 | 92%
|  |  | T5HO Fluorescent | 70% | T5HO Fluorescent-0.7 | 91.5 | 91.5%
|  |  | T5HO Fluorescent | 80% | T5HO Fluorescent-0.8 | 91 | 91%
|  |  | T5HO Fluorescent | 90% | T5HO Fluorescent-0.9 | 90.5 | 90.5%
|  |  | T5HO Fluorescent | 100% | T5HO Fluorescent-1 | 90 | 90%
|  |  | T12 Fluorescent | 0% | T12 Fluorescent-0 | 100 | 100%
|  |  | T12 Fluorescent | 10% | T12 Fluorescent-0.1 | 95 | 95%
|  |  | T12 Fluorescent | 20% | T12 Fluorescent-0.2 | 91 | 91%
|  |  | T12 Fluorescent | 30% | T12 Fluorescent-0.3 | 87 | 87%
|  |  | T12 Fluorescent | 40% | T12 Fluorescent-0.4 | 85 | 85%
|  |  | T12 Fluorescent | 50% | T12 Fluorescent-0.5 | 81 | 81%
|  |  | T12 Fluorescent | 60% | T12 Fluorescent-0.6 | 79 | 79%
|  |  | T12 Fluorescent | 70% | T12 Fluorescent-0.7 | 77.5 | 77.5%
|  |  | T12 Fluorescent | 80% | T12 Fluorescent-0.8 | 76 | 76%
|  |  | T12 Fluorescent | 90% | T12 Fluorescent-0.9 | 75 | 75%
|  |  | T12 Fluorescent | 100% | T12 Fluorescent-1 | 74 | 74%
|  |  | High Pressure Sodium | 0% | High Pressure Sodium-0 | 100 | 100%
|  |  | High Pressure Sodium | 10% | High Pressure Sodium-0.1 | 97 | 97%
|  |  | High Pressure Sodium | 20% | High Pressure Sodium-0.2 | 95 | 95%
|  |  | High Pressure Sodium | 30% | High Pressure Sodium-0.3 | 93 | 93%
|  |  | High Pressure Sodium | 40% | High Pressure Sodium-0.4 | 91 | 91%
|  |  | High Pressure Sodium | 50% | High Pressure Sodium-0.5 | 87 | 87%
|  |  | High Pressure Sodium | 60% | High Pressure Sodium-0.6 | 85 | 85%
|  |  | High Pressure Sodium | 70% | High Pressure Sodium-0.7 | 81 | 81%
|  |  | High Pressure Sodium | 80% | High Pressure Sodium-0.8 | 77 | 77%
|  |  | High Pressure Sodium | 90% | High Pressure Sodium-0.9 | 74 | 74%
|  |  | High Pressure Sodium | 100% | High Pressure Sodium-1 | 70 | 70%
|  |  | Probe Start Metal Halide | 0% | Probe Start Metal Halide-0 | 100 | 100%
|  |  | Probe Start Metal Halide | 10% | Probe Start Metal Halide-0.1 | 89 | 89%
|  |  | Probe Start Metal Halide | 20% | Probe Start Metal Halide-0.2 | 79 | 79%
|  |  | Probe Start Metal Halide | 30% | Probe Start Metal Halide-0.3 | 72 | 72%
|  |  | Probe Start Metal Halide | 40% | Probe Start Metal Halide-0.4 | 64 | 64%
|  |  | Probe Start Metal Halide | 50% | Probe Start Metal Halide-0.5 | 58 | 58%
|  |  | Probe Start Metal Halide | 60% | Probe Start Metal Halide-0.6 | 54 | 54%
|  |  | Probe Start Metal Halide | 70% | Probe Start Metal Halide-0.7 | 51 | 51%
|  |  | Probe Start Metal Halide | 80% | Probe Start Metal Halide-0.8 | 48 | 48%
|  |  | Probe Start Metal Halide | 90% | Probe Start Metal Halide-0.9 | 44 | 44%
|  |  | Probe Start Metal Halide | 100% | Probe Start Metal Halide-1 | 41 | 41%
|  |  | Pulse Start Metal Halide | 0% | Pulse Start Metal Halide-0 | 100 | 100%
|  |  | Pulse Start Metal Halide | 10% | Pulse Start Metal Halide-0.1 | 93 | 93%
|  |  | Pulse Start Metal Halide | 20% | Pulse Start Metal Halide-0.2 | 86 | 86%
|  |  | Pulse Start Metal Halide | 30% | Pulse Start Metal Halide-0.3 | 79 | 79%
|  |  | Pulse Start Metal Halide | 40% | Pulse Start Metal Halide-0.4 | 75 | 75%
|  |  | Pulse Start Metal Halide | 50% | Pulse Start Metal Halide-0.5 | 71 | 71%
|  |  | Pulse Start Metal Halide | 60% | Pulse Start Metal Halide-0.6 | 69 | 69%
|  |  | Pulse Start Metal Halide | 70% | Pulse Start Metal Halide-0.7 | 65 | 65%
|  |  | Pulse Start Metal Halide | 80% | Pulse Start Metal Halide-0.8 | 63 | 63%
|  |  | Pulse Start Metal Halide | 90% | Pulse Start Metal Halide-0.9 | 60 | 60%
|  |  | Pulse Start Metal Halide | 100% | Pulse Start Metal Halide-1 | 58 | 58%
|  |  | Electronic Pulse Start Metal Halide | 0% | Electronic Pulse Start Metal Halide-0 | 100 | 100%
|  |  | Electronic Pulse Start Metal Halide | 10% | Electronic Pulse Start Metal Halide-0.1 | 94 | 94%
|  |  | Electronic Pulse Start Metal Halide | 20% | Electronic Pulse Start Metal Halide-0.2 | 90 | 90%
|  |  | Electronic Pulse Start Metal Halide | 30% | Electronic Pulse Start Metal Halide-0.3 | 88 | 88%
|  |  | Electronic Pulse Start Metal Halide | 40% | Electronic Pulse Start Metal Halide-0.4 | 86 | 86%
|  |  | Electronic Pulse Start Metal Halide | 50% | Electronic Pulse Start Metal Halide-0.5 | 85 | 85%
|  |  | Electronic Pulse Start Metal Halide | 60% | Electronic Pulse Start Metal Halide-0.6 | 84 | 84%
|  |  | Electronic Pulse Start Metal Halide | 70% | Electronic Pulse Start Metal Halide-0.7 | 83 | 83%
|  |  | Electronic Pulse Start Metal Halide | 80% | Electronic Pulse Start Metal Halide-0.8 | 82 | 82%
|  |  | Electronic Pulse Start Metal Halide | 90% | Electronic Pulse Start Metal Halide-0.9 | 81 | 81%
|  |  | Electronic Pulse Start Metal Halide | 100% | Electronic Pulse Start Metal Halide-1 | 80 | 80%
|  |  | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
|  | T8 Fluorescent | 100 | 98 | 96 | 95.5 | 95 | 94.5 | 94 | 93.5 | 93 | 92.5 | 92
|  | T5HO Fluorescent | 100 | 98 | 96 | 95 | 94 | 93 | 92 | 91.5 | 91 | 90.5 | 90
|  | T12 Fluorescent | 100 | 95 | 91 | 87 | 85 | 81 | 79 | 77.5 | 76 | 75 | 74
|  | High Pressure Sodium | 100 | 97 | 95 | 93 | 91 | 87 | 85 | 81 | 77 | 74 | 70
Advance |  | Probe Start Metal Halide | 100 | 89 | 79 | 72 | 64 | 58 | 54 | 51 | 48 | 44 | 41
Advance |  | Pulse Start Metal Halide | 100 | 93 | 86 | 79 | 75 | 71 | 69 | 65 | 63 | 60 | 58
Advance |  | Electronic Pulse Start Metal Halide | 100 | 94 | 90 | 88 | 86 | 85 | 84 | 83 | 82 | 81 | 80
|  | 150W Elec PSMH | 0%: 13300; 10%: 0.9; 20%: 1; 30%: Electronic Pulse Start Metal Halide
|  | 175W Elec PSMH | 0%: 17500; 10%: 0.9; 20%: 1; 30%: Electronic Pulse Start Metal Halide
|  | 150W PSMH | 0%: 13300; 10%: 0.8; 20%: 1; 30%: Pulse Start Metal Halide
|  | 175W PSMH | 0%: 17500; 10%: 0.8; 20%: 1; 30%: Pulse Start Metal Halide
|  | 175W MH | 0%: 13600; 10%: 0.58; 20%: 1; 30%: Probe Start Metal Halide
|  | 150W HPS | 0%: 16000; 10%: 0.81; 20%: 1; 30%: High Pressure Sodium
Note on E28: Based on reflectances of 50,50,20
Note on E37: Maintained Illuminance on Proposed System is based on 40% of rated life.
Note on E164: Administrator: DIM
Note on E165: Administrator: SN
Note on E167: Administrator: G
Note on E168: Administrator: 18C

## 10 Yr Maintenance Costs
Insert Logo Here
Annual Maintenance Cost Estimator: 10 Year Breakdown
Input
Output
Customer Information |  |  |  | Facility Information
Project Name:
Contact: |  |  |  | Annual Operating Hours | 8760
System Information |  |  | Existing System |  | Proposed System
Description of System
Quantity
| Type of Lamp |  | Please Select |  | Please Select
Lamp Life (hrs)
Cost of Lamp
| Number of Lamps Per Fixture |  | Please Select |  | Please Select
Labor Cost to Spot Relamp per Lamp
Annual Lamp Maintenance Cost
Quantity of Lamps Replaced Annually
| Ballast Type |  | Please Select |  | Please Select
Ballast Life (hrs)
Cost of Ballast
| Number of Ballasts Per Fixture |  | Please Select |  | Please Select
Labor Cost Change a Ballast
Annual Ballast Maintenance Cost
Quantity of Ballasts Replaced Annually
Annual Maintenance Cost of System at Maturity
| Summarized 10 Year Cost |  | #VALUE! |  | 0
| 10 Year Savings Summary |  |  |  | #VALUE!
10 Year Average Annual Savings Summary |  |  |  |  | #VALUE!
Based on Existing System at Maturity and Proposed System with Lamp Maintenance at 3 Years and Ballast Maintenance at 5 Years.
Note: These are estimated savings only based on a number of variables and assumptions that could change over time. The actual savings derived may be higher or lower.
Return to TOP
Return to HOME
[10 empty] | Total # Ballasts | #VALUE!
| Maintenance Costs (Yr) |  | Existing Lamps |  | Existing Ballasts | Existing Maintenance | Proposed Lamps | Proposed Ballast | Proposed Maintenance | Ballast Life Hours
| 1 |  |  |  |  | #VALUE! |  |  | 0
| 2 |  |  |  |  | #VALUE! |  |  | 0
| 3 |  |  |  |  | #VALUE! |  |  | #VALUE!
| 4 |  |  |  |  | #VALUE! |  |  | #VALUE!
| 5 |  |  |  |  | #VALUE! |  |  | #VALUE!
| 6 |  |  |  |  | #VALUE! |  |  | #VALUE!
| 7 |  |  |  |  | #VALUE! |  |  | #VALUE!
| 8 |  |  |  |  | #VALUE! |  |  | #VALUE!
| 9 |  |  |  |  | #VALUE! |  |  | #VALUE!
| 10 |  |  |  |  | #VALUE! |  |  | #VALUE!
|  |  | 0 |  | 0 | 0 | 0 | 0 | 0
| Please Select | Lamp Life |  | ULT Warranty in Months (.95 survival rate) |  | ULT Warranty in Hrs | ULT Warranty in Hrs X2 |  |  |  |  | Input Watts
| HID, HPS | 24000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 130
| HID, 175W MH | 10000 |  | 2 | 8760 | 17520 | 35040
| HID, 250W MH | 10000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 129
| HID, 400W MH | 20000 |  | 2 | 8760 | 17520 | 35040
| HID, 1000W MH | 15000 |  | 2 | 8760 | 17520 | 35040
| HID, 250W PSMH | 15000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 189
| HID, 175W PSMH | 15000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 208
| HID, 150W PSMH | 15000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 288
| HID, 320W PSMH | 20000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 368
| HID, 350W PSMH | 20000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 400
| HID, 400W PSMH | 20000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 448
| HID, 750W PSMH | 16000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 820
| HID, 1000W PSMH | 12000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 1080
| HID, 70W ECON PSMH | 15000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 80
| HID, 100W ECON PSMH | 10000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 110
| HID, 150W ECON PSMH | 12000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 169
| HID, 200W ECON PSMH | 15000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 194
| HID, 250W ECON PSMH | 15000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 229
| HID, 175W ECON PSMH | 15000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 285
| HID, 320W ECON PSMH | 30000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 330
| HID, 350W ECON PSMH | 30000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 375
| HID, 400W ECON PSMH | 30000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 430
| HID, 450W ECON PSMH | 30000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 478
| HID, CMH | 20000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 272
| Fluorescent, T12 | 20000 |  | 3 | 8760 | 26280 | 52560 |  |  |  |  | 135
| Fluorescent, T12 HO/SL | 12000 |  | 3 | 8760 | 26280 | 52560 |  |  |  |  | 180
| Fluorescent, T12 U Lamp | 14000 |  | 3 | 8760 | 26280 | 52560 |  |  |  |  | 44
| Fluorescent, T12 VHO | 9000 |  | 3 | 8760 | 26280 | 52560 |  |  |  |  | 138
| Fluorescent, T5 | 30000 |  | 5 | 8760 | 43800 | 87600 |  |  |  |  | 25
| Fluorescent, T5 HO | 30000 |  | 5 | 8760 | 43800 | 87600 |  |  |  |  | 110
| Fluorescent, T8 | 20000 |  | 5 | 8760 | 43800 | 87600 |  |  |  |  | 182
| Fluorsecent, T8 Extra Life | 30000
| Fluorescent, T8 U Lamp | 20000 |  | 5 | 8760 | 43800 | 87600 |  |  |  |  | 34
| Compact Fluorescent, PL-H | 20000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 417
| Compact Fluorescent, Double/Triple Biax | 12000 |  | 2 | 8760 | 17520 | 35040 |  |  |  |  | 18
Please Select
1
2
3
4
6
8
| Please Select | Ballast Life
| Energy Efficient Magnetic | 60000
| Magnetic | 60000
| Programmed Start HPF | 80000
| Programmed Start LPF | 80000
| Programmed Start NPF | 80000
| Instant Start HPF | 80000
| Instant Start LPF | 80000
| Instant Start NPF | 80000
| CWA | 60000
| CWI | 60000
| Electronic HID | 80000
| High Reactance | 60000
| Reactor | 60000
| N/A | 0
Note on B36: This caclulation assumes both systems are aged and spot relamping is occuring
Note on C19: Assumed at 3 hrs per Start for FLR, 10 hrs per Start for HID
Note on C20: Costs should include purchase price and recycling/disposal costs
Note on C29: Costs should include purchase price and recycling/disposal costs
Note on C37: This calculation looks at the avoided average labor costs over 10 years and is inclusive of no maintenance on lamps for the 1st three years and no ballast maintenance for the first 5 years.

## Maintenance Costs
Insert Logo Here
Annual Maintenance Cost Estimator: Existing System
Input
Output
Customer Information |  |  | Facility Information
Project Name:
Contact: |  |  | Annual Operating Hours
System Information
Description of System
Quantity
|  | Type of Lamp | Please Select
|  | Lamp Life (hrs) | #N/A
Cost of Lamp
|  | Number of Lamps Per Fixture | Please Select
Labor Cost to Spot Relamp per Lamp
|  | Annual Lamp Maintenance Cost | #N/A
|  | Quantity of Lamps Replaced Annually | #N/A
|  | Ballast Type | Please Select
|  | Ballast Life (hrs) | #N/A
Cost of Ballast
|  | Number of Ballasts Per Fixture | Please Select
Labor Cost Change a Ballast
|  | Annual Ballast Maintenance Cost | #N/A
|  | Quantity of Ballasts Replaced Annually | #N/A
|  | Annual Maintenance Cost of System | #N/A
Note: These are estimated savings only based on a number of variables and assumptions that could change over time. The actual savings derived may be higher or lower.
Return to TOP
Return to HOME
| Please Select | Lamp Life | ULT Warranty in Months (.95 survival rate) |  | ULT Warranty in Hrs | ULT Warranty in Hrs X2 | Input Watts
| HID, HPS | 24000 | 2 | 8760 | 17520 | 35040 | 130
| HID, 175W MH | 10000 | 2 | 8760 | 17520 | 35040
| HID, 250W MH | 10000 | 2 | 8760 | 17520 | 35040 | 129
| HID, 400W MH | 20000 | 2 | 8760 | 17520 | 35040
| HID, 1000W MH | 15000 | 2 | 8760 | 17520 | 35040
| HID, 250W PSMH | 15000 | 2 | 8760 | 17520 | 35040 | 189
| HID, 175W PSMH | 15000 | 2 | 8760 | 17520 | 35040 | 208
| HID, 150W PSMH | 15000 | 2 | 8760 | 17520 | 35040 | 288
| HID, 320W PSMH | 20000 | 2 | 8760 | 17520 | 35040 | 368
| HID, 350W PSMH | 20000 | 2 | 8760 | 17520 | 35040 | 400
| HID, 400W PSMH | 20000 | 2 | 8760 | 17520 | 35040 | 448
| HID, 750W PSMH | 16000 | 2 | 8760 | 17520 | 35040 | 820
| HID, 1000W PSMH | 12000 | 2 | 8760 | 17520 | 35040 | 1080
| HID, 70W ECON PSMH | 15000 | 2 | 8760 | 17520 | 35040 | 80
| HID, 100W ECON PSMH | 10000 | 2 | 8760 | 17520 | 35040 | 110
| HID, 150W ECON PSMH | 12000 | 2 | 8760 | 17520 | 35040 | 169
| HID, 200W ECON PSMH | 15000 | 2 | 8760 | 17520 | 35040 | 194
| HID, 250W ECON PSMH | 15000 | 2 | 8760 | 17520 | 35040 | 229
| HID, 175W ECON PSMH | 15000 | 2 | 8760 | 17520 | 35040 | 285
| HID, 320W ECON PSMH | 30000 | 2 | 8760 | 17520 | 35040 | 330
| HID, 350W ECON PSMH | 30000 | 2 | 8760 | 17520 | 35040 | 375
| HID, 400W ECON PSMH | 30000 | 2 | 8760 | 17520 | 35040 | 430
| HID, 450W ECON PSMH | 30000 | 2 | 8760 | 17520 | 35040 | 478
| HID, CMH | 20000 | 2 | 8760 | 17520 | 35040 | 272
| Fluorescent, T12 | 20000 | 3 | 8760 | 26280 | 52560 | 135
| Fluorescent, T12 HO/SL | 12000 | 3 | 8760 | 26280 | 52560 | 180
| Fluorescent, T12 U Lamp | 14000 | 3 | 8760 | 26280 | 52560 | 44
| Fluorescent, T12 VHO | 9000 | 3 | 8760 | 26280 | 52560 | 138
| Fluorescent, T5 | 30000 | 5 | 8760 | 43800 | 87600 | 25
| Fluorescent, T5 HO | 30000 | 5 | 8760 | 43800 | 87600 | 110
| Fluorescent, T8 | 20000 | 5 | 8760 | 43800 | 87600 | 182
| Fluorsecent, T8 Extra Life | 30000
| Fluorescent, T8 U Lamp | 20000 | 5 | 8760 | 43800 | 87600 | 34
| Compact Fluorescent, PL-H | 20000 | 2 | 8760 | 17520 | 35040 | 417
| Compact Fluorescent, Double/Triple Biax | 12000 | 2 | 8760 | 17520 | 35040 | 18
Please Select
1
2
3
4
6
8
| Please Select | Ballast Life
| Energy Efficient Magnetic | 60000
| Magnetic | 60000
| Programmed Start HPF | 80000
| Programmed Start LPF | 80000
| Programmed Start NPF | 80000
| Instant Start HPF | 80000
| Instant Start LPF | 80000
| Instant Start NPF | 80000
| CWA | 60000
| CWI | 60000
| Electronic HID | 80000
| High Reactance | 60000
| Reactor | 60000
| N/A | 0
Note on D19: Assumed at 3 hrs per Start for FLR, 10 hrs per Start for HID
Note on D20: Costs should include purchase price and recycling/disposal costs
Note on D29: Costs should include purchase price and recycling/disposal costs

## Maintenance Factors
Insert Logo Here
Maintenance Factors
Letter Assignment According to Luminaire's Environment & CIE Classification
CIE Classification |  |  | Direct | Semi-Direct | General Diffuse | Semi-Indirect | Indirect
|  | % Uplight | 0-10 | 10-40 | 40-60 | 60-90 | 90-100
|  | % Downlight | 90-100 | 60-90 | 40-60 | 10-40 | 0-10
Environment | Clean | Open / Unventiliated | W | W | W | X | X
|  | All Other | W | W | W | X | X
| Moderate | Open / Unventiliated | XY | XY | XY | Y | Y
|  | All Other | X | X | X | Y | Y
| Dirty | Open / Unventiliated | Z | Z | Z | Z | Z
|  | All Other | Y | Y | Y | Y | Y
Tables & charts adapted from the IESNA/NALMCO RP-36-03 guidelines.
Return to TOP
Return to HOME
|  |  | 0 | 20 | 40 | 60 | 80 | 100
|  | Halogen Incandescent | 100 | 99 | 97 | 96 | 95 | 94
|  | T8 Fluorescent | 100 | 96 | 95 | 94 | 93 | 92
|  | T5 & T5HO Fluorescent | 100 | 96 | 94 | 92 | 91 | 90
|  | Incandescent | 100 | 96 | 91 | 87 | 84 | 81
|  | T12 Fluorescent | 100 | 91 | 85 | 80 | 76 | 74
|  | High Pressure Sodium | 100 | 90 | 84 | 79 | 75 | 69
|  | Metal Halide & Mercury Vapor | 100 | 89 | 78 | 70 | 63 | 56
|  | Pulse Start Metal Halide | 100 | 86 | 75 | 69 | 63 | 58
|  | Electronic PSMH | 100 | 90 | 86 | 84 | 82 | 80
|  |  | 0 |  | 6 |  | 12 |  | 18 |  | 24 |  | 30 |  | 36 |  | 42 |  | 48
|  | W | 1 | 0.975 | 0.95 | 0.94 | 0.93 | 0.92 | 0.915 | 0.905 | 0.9 | 0.9 | 0.9 | 0.895 | 0.89 | 0.885 | 0.88 | 0.88 | 0.88
|  | WX |  |  | 0.95 | 0.925 | 0.9 | 0.895 | 0.89 | 0.88 | 0.87 | 0.86 | 0.85 | 0.845 | 0.84 | 0.845 | 0.83 | 0.825 | 0.82
|  | X |  |  | 0.95 | 0.925 | 0.9 | 0.885 | 0.87 | 0.86 | 0.85 | 0.835 | 0.82 | 0.81 | 0.8 | 0.79 | 0.78 | 0.775 | 0.77
|  | XY | 0.98 | 0.94 | 0.9 | 0.88 | 0.85 | 0.835 | 0.82 | 0.805 | 0.79 | 0.78 | 0.77 | 0.755 | 0.74 | 0.73 | 0.72 | 0.715 | 0.71
|  | Y | 0.97 | 0.91 | 0.85 | 0.825 | 0.8 | 0.77 | 0.75 | 0.735 | 0.72 | 0.71 | 0.7 | 0.675 | 0.66 | 0.655 | 0.65 | 0.645 | 0.64
|  | YZ |  |  | 0.85 | 0.81 | 0.76 | 0.73 | 0.7 | 0.68 | 0.66 | 0.635 | 0.6 | 0.585 | 0.57 | 0.555 | 0.54 | 0.52 | 0.5
|  | Z |  |  | 0.85 | 0.785 | 0.72 | 0.685 | 0.65 | 0.62 | 0.59 | 0.56 | 0.53 | 0.495 | 0.46 | 0.445 | 0.43 | 0.41

## ProductivityImpact
Insert Your Logo Here | Productivity Impact of Lighting Upgrade
Input
Output
Customer Information
Project Name:
Contact:
Lighting System Details
Capital Investment:
Estimated Payroll Expense:
|  | Estimated Productivity Increase (%): | 3%
|  | Productivity Impact of Lighting System Upgrade: | 0
|  | Productivity Payback: | #DIV/0!
The aggregate of 25 studies on lighting and worker productivity have demonstrated that high perofrmance lighting sytems used in coordination with daylighting raised productivity levels from .7% to 26% with a median improvement of 3%. This is only an estimate. Actual productivity levels are dependent on factors not necessarily included in this simple calculation.
Return to HOME

## HVAC
Insert Logo Here
HVAC Energy Savings from Lighting System Retrofit
Input
Output
Customer Information
Project Name: |  |  |  | Contact:
System Information
Lighting Energy Savings (per Month)
|  | State, City |  | Please Select
|  | Cooling Months |  | Months | 0
|  | ASHRAE Factor |  | 0.35
| Energy Savings from HVAC System Based on Lighting Retrofit (per Month) |  |  | #DIV/0!
Values and Calculations are based on the method described in Rundquist, 1993, ASHRAE Method. Controlling Energy Consumption in Single Buildings, U.S. Department of the Navy, Naval Civil Engineering Lab, CR82.028, 1982
Return to HOME
ST |  | State | City | Please Select | Weeks | Months | Rounded
AL |  | Alabama | Birmingham | Alabama, Birmingham | 32.9 | 7.5929 | 8 | 0
|  | Alabama | Huntsville | Alabama, Huntsville | 30.9 | 7.1313 | 7 | 0
|  | Alabama | Mobile | Alabama, Mobile | 38.4 | 8.8622 | 9 | 0
|  | Alabama | Montgomery | Alabama, Montgomery | 35.3 | 8.1468 | 8 | 0
AZ |  | Arizona | Flagstaff | Arizona, Flagstaff | 18.6 | 4.2926 | 4 | 0
|  | Arizona | Phoenix | Arizona, Phoenix | 41.3 | 9.5315 | 10 | 0
|  | Arizona | Tucson | Arizona, Tucson | 40.1 | 9.2546 | 9 | 0
AR |  | Arkansas | Blytheville | Arkansas, Blytheville | 29.7 | 6.8544 | 7 | 0
|  | Arkansas | Fort Smith | Arkansas, Fort Smith | 30.5 | 7.039 | 7 | 0
|  | Arkansas | Little Rock | Arkansas, Little Rock | 29.7 | 6.8544 | 7 | 0
CA |  | California | Barstow | California, Barstow | 32.2 | 7.4313 | 7 | 0
|  | California | Bishop | California, Bishop | 30.4 | 7.0159 | 7 | 0
|  | California | Los Angeles | California, Los Angeles | 32.6 | 7.5237 | 8 | 0
|  | California | Sacramento | California, Sacramento | 28.4 | 6.5544 | 7 | 0
|  | California | San Diego | California, San Diego | 29.8 | 6.8775 | 7 | 0
|  | California | San Francisco | California, San Francisco | 22.2 | 5.1235 | 5 | 0
|  | California | Santa Barbara | California, Santa Barbara | 12.2 | 2.8156 | 3 | 0
CO |  | Colorado | Colorado Springs | Colorado, Colorado Springs | 21.6 | 4.985 | 5 | 0
|  | Colorado | Denver | Colorado, Denver | 22.6 | 5.2158 | 5 | 0
|  | Colorado | Grand Junction | Colorado, Grand Junction | 23.7 | 5.4697 | 5 | 0
|  | Colorado | Trinidad | Colorado, Trinidad | 25.4 | 5.862 | 6 | 0
CT |  | Connecticut | Hartford | Connecticut, Hartford | 20 | 4.6157 | 5 | 0
DE |  | Delaware | Dover | Delaware, Dover | 23.6 | 5.4466 | 5 | 0
|  | Delaware | Wilmington | Delaware, Wilmington | 23.7 | 5.4697 | 5 | 0
DC |  | District Of Columbia | Washington | District Of Columbia, Washington | 26 | 6.0005 | 6 | 0
FL |  | Florida | Jacksonville | Florida, Jacksonville | 41.6 | 9.6007 | 10 | 0
|  | Florida | Miami | Florida, Miami | 50.1 | 11.5624 | 12 | 0
|  | Florida | Orlando | Florida, Orlando | 46.2 | 10.6624 | 11 | 0
|  | Florida | Pensacola | Florida, Pensacola | 38.4 | 8.8622 | 9 | 0
|  | Florida | Tampa | Florida, Tampa | 46 | 10.6162 | 11 | 0
GA |  | Georgia | Atlanta | Georgia, Atlanta | 30 | 6.9236 | 7 | 0
|  | Georgia | Augusta | Georgia, Augusta | 35.1 | 8.1006 | 8 | 0
|  | Georgia | Macon | Georgia, Macon | 34.8 | 8.0314 | 8 | 0
|  | Georgia | Savannah | Georgia, Savannah | 38 | 8.7699 | 9 | 0
|  | Georgia | Valdosta | Georgia, Valdosta | 38.9 | 8.9776 | 9 | 0
ID |  | Idaho | Boise | Idaho, Boise | 19.7 | 4.5465 | 5 | 0
|  | Idaho | Lewiston | Idaho, Lewiston | 18.9 | 4.3619 | 4 | 0
|  | Idaho | Pocatello | Idaho, Pocatello | 18.8 | 4.3388 | 4 | 0
IL |  | Illinois | Champaign | Illinois, Champaign | 23.6 | 5.4466 | 5 | 0
|  | Illinois | Chicago | Illinois, Chicago | 20.9 | 4.8234 | 5 | 0
|  | Illinois | Peoria | Illinois, Peoria | 24 | 5.5389 | 6 | 0
|  | Illinois | Rockford | Illinois, Rockford | 21 | 4.8465 | 5 | 0
IN |  | Indiana | Fort Wayne | Indiana, Fort Wayne | 22.5 | 5.1927 | 5 | 0
|  | Indiana | Indianapolis | Indiana, Indianapolis | 23.9 | 5.5158 | 6 | 0
|  | Indiana | South Bend | Indiana, South Bend | 21.4 | 4.9388 | 5 | 0
|  | Indiana | Terre Haute | Indiana, Terre Haute | 24.8 | 5.7235 | 6 | 0
IA |  | Iowa | Council Bluffs | Iowa, Council Bluffs | 23 | 5.3081 | 5 | 0
|  | Iowa | Mason City | Iowa, Mason City | 19.7 | 4.5465 | 5 | 0
|  | Iowa | Sioux City | Iowa, Sioux City | 22.2 | 5.1235 | 5 | 0
KS |  | Kansas | Dodge City | Kansas, Dodge City | 25.6 | 5.9081 | 6 | 0
|  | Kansas | Goodland | Kansas, Goodland | 23.6 | 5.4466 | 5 | 0
|  | Kansas | Kansas City | Kansas, Kansas City | 25.7 | 5.9312 | 6 | 0
|  | Kansas | Wichita | Kansas, Wichita | 27 | 6.2312 | 6 | 0
KY |  | Kentucky | Covington | Kentucky, Covington | 24.4 | 5.6312 | 6 | 0
|  | Kentucky | Hopkinsville | Kentucky, Hopkinsville | 28.4 | 6.5544 | 7 | 0
|  | Kentucky | Louisville | Kentucky, Louisville | 26.6 | 6.1389 | 6 | 0
LA |  | Louisiana | Alexandria | Louisiana, Alexandria | 37.2 | 8.5853 | 9 | 0
|  | Louisiana | Lake Charles | Louisiana, Lake Charles | 39.2 | 9.0468 | 9 | 0
|  | Louisiana | New Orleans | Louisiana, New Orleans | 39.6 | 9.1392 | 9 | 0
|  | Louisiana | Shreveport | Louisiana, Shreveport | 35.2 | 8.1237 | 8 | 0
ME |  | Maine | Portland | Maine, Portland | 15.5 | 3.5772 | 4 | 0
MA |  | Massachusetts | Boston | Massachusetts, Boston | 19.8 | 4.5696 | 5 | 0
|  | Massachusetts | Springfield | Massachusetts, Springfield | 20.1 | 4.6388 | 5 | 0
MD |  | Maryland | Baltimore | Maryland, Baltimore | 25 | 5.7697 | 6 | 0
MI |  | Michigan | Detroit | Michigan, Detroit | 19.2 | 4.4311 | 4 | 0
|  | Michigan | Grand Rapids | Michigan, Grand Rapids | 19 | 4.385 | 4 | 0
|  | Michigan | Lansing | Michigan, Lansing | 19.5 | 4.5003 | 5 | 0
|  | Michigan | Sault St Marie | Michigan, Sault St Marie | 12.8 | 2.9541 | 3 | 0
|  | Michigan | Travarse City | Michigan, Travarse City | 17 | 3.9234 | 4 | 0
MN |  | Minnesota | Duluth | Minnesota, Duluth | 12.7 | 2.931 | 3 | 0
|  | Minnesota | Internat'l Falls | Minnesota, Internat'l Falls | 14.1 | 3.2541 | 3 | 0
|  | Minnesota | Minneapolis | Minnesota, Minneapolis | 18.8 | 4.3388 | 4 | 0
MS |  | Mississippi | Biloxi | Mississippi, Biloxi | 37.6 | 8.6776 | 9 | 0
|  | Mississippi | Columbus | Mississippi, Columbus | 33.8 | 7.8006 | 8 | 0
|  | Mississippi | Jackson | Mississippi, Jackson | 35.3 | 8.1468 | 8 | 0
MO |  | Missouri | Columbia | Missouri, Columbia | 25.7 | 5.9312 | 6 | 0
|  | Missouri | Kansas City | Missouri, Kansas City | 25.7 | 5.9312 | 6 | 0
|  | Missouri | Springfield | Missouri, Springfield | 26.9 | 6.2082 | 6 | 0
|  | Missouri | St. Louis | Missouri, St. Louis | 26.3 | 6.0697 | 6 | 0
MT |  | Montana | Billings | Montana, Billings | 18.4 | 4.2465 | 4 | 0
|  | Montana | Glasgow | Montana, Glasgow | 17.5 | 4.0388 | 4 | 0
|  | Montana | Great Falls | Montana, Great Falls | 16.9 | 3.9003 | 4 | 0
|  | Montana | Helena | Montana, Helena | 15.5 | 3.5772 | 4 | 0
NE |  | Nebraska | Grand Island | Nebraska, Grand Island | 22.7 | 5.2389 | 5 | 0
|  | Nebraska | North Platt | Nebraska, North Platt | 22 | 5.0773 | 5 | 0
|  | Nebraska | Omaha | Nebraska, Omaha | 23 | 5.3081 | 5 | 0
NV |  | Nevada | Ely | Nevada, Ely | 20.2 | 4.6619 | 5 | 0
|  | Nevada | Las Vegas | Nevada, Las Vegas | 35.4 | 8.1699 | 8 | 0
|  | Nevada | Reno | Nevada, Reno | 21 | 4.8465 | 5 | 0
|  | Nevada | Winnemucca | Nevada, Winnemucca | 22.3 | 5.1465 | 5 | 0
NH |  | New Hampshire | Manchester | New Hampshire, Manchester | 19 | 4.385 | 4 | 0
NJ |  | New Jersey | Trenton | New Jersey, Trenton | 22.9 | 5.285 | 5 | 0
NM |  | New Mexico | Alburquerque | New Mexico, Alburquerque | 27.3 | 6.3005 | 6 | 0
|  | New Mexico | Alamogordo | New Mexico, Alamogordo | 32.5 | 7.5006 | 8 | 0
|  | New Mexico | Clovis | New Mexico, Clovis | 29.4 | 6.7851 | 7 | 0
NY |  | New York | Albany | New York, Albany | 19.5 | 4.5003 | 5 | 0
|  | New York | Buffalo | New York, Buffalo | 18.8 | 4.3388 | 4 | 0
|  | New York | New York City | New York, New York City | 20 | 4.6157 | 5 | 0
|  | New York | Syracuse | New York, Syracuse | 19.4 | 4.4773 | 4 | 0
NC |  | North Carolina | Greensboro | North Carolina, Greensboro | 28.1 | 6.4851 | 6 | 0
|  | North Carolina | Raleigh | North Carolina, Raleigh | 30 | 6.9236 | 7 | 0
|  | North Carolina | Wilmington | North Carolina, Wilmington | 33.6 | 7.7544 | 8 | 0
ND |  | North Dakota | Bismarck | North Dakota, Bismarck | 18.3 | 4.2234 | 4 | 0
|  | North Dakota | Fargo | North Dakota, Fargo | 17 | 3.9234 | 4 | 0
|  | North Dakota | Grand Forks | North Dakota, Grand Forks | 16.9 | 3.9003 | 4 | 0
|  | North Dakota | Minot | North Dakota, Minot | 16.2 | 3.7387 | 4 | 0
OH |  | Ohio | Cincinnati | Ohio, Cincinnati | 24.2 | 5.585 | 6 | 0
|  | Ohio | Cleveland | Ohio, Cleveland | 21 | 4.8465 | 5 | 0
|  | Ohio | Columbus | Ohio, Columbus | 23.8 | 5.4927 | 5 | 0
|  | Ohio | Dayton | Ohio, Dayton | 24.3 | 5.6081 | 6 | 0
|  | Ohio | Toledo | Ohio, Toledo | 21.3 | 4.9158 | 5 | 0
OK |  | Oklahoma | Altus | Oklahoma, Altus | 31.2 | 7.2006 | 7 | 0
|  | Oklahoma | Enid | Oklahoma, Enid | 28.4 | 6.5544 | 7 | 0
|  | Oklahoma | Oklahoma City | Oklahoma, Oklahoma City | 29.5 | 6.8082 | 7 | 0
|  | Oklahoma | Tulsa | Oklahoma, Tulsa | 29.7 | 6.8544 | 7 | 0
OR |  | Oregon | Burns | Oregon, Burns | 17.3 | 3.9926 | 4 | 0
|  | Oregon | Eugene | Oregon, Eugene | 15 | 3.4618 | 3 | 0
|  | Oregon | Medford | Oregon, Medford | 21.2 | 4.8927 | 5 | 0
|  | Oregon | Pendleton | Oregon, Pendleton | 20 | 4.6157 | 5 | 0
|  | Oregon | Portland | Oregon, Portland | 15.8 | 3.6464 | 4 | 0
PA |  | Pennsylvania | Philadelphia | Pennsylvania, Philadelphia | 23.7 | 5.4697 | 5 | 0
|  | Pennsylvania | Pittsburgh | Pennsylvania, Pittsburgh | 21.9 | 5.0542 | 5 | 0
|  | Pennsylvania | Scranton | Pennsylvania, Scranton | 20.1 | 4.6388 | 5 | 0
|  | Pennsylvania | Williamsport | Pennsylvania, Williamsport | 21 | 4.8465 | 5 | 0
RI |  | Rhode Island | Providence | Rhode Island, Providence | 18.7 | 4.3157 | 4 | 0
SC |  | South Carolina | Charleston | South Carolina, Charleston | 36 | 8.3083 | 8 | 0
|  | South Carolina | Columbia | South Carolina, Columbia | 33.4 | 7.7083 | 8 | 0
|  | South Carolina | Myrtle Beach | South Carolina, Myrtle Beach | 32.3 | 7.4544 | 7 | 0
SD |  | South Dakota | Huron | South Dakota, Huron | 20.4 | 4.7081 | 5 | 0
|  | South Dakota | Rapid City | South Dakota, Rapid City | 19.6 | 4.5234 | 5 | 0
|  | South Dakota | Sioux Falls | South Dakota, Sioux Falls | 20.5 | 4.7311 | 5 | 0
TN |  | Tennessee | Knoxville | Tennessee, Knoxville | 29 | 6.6928 | 7 | 0
|  | Tennessee | Memphis | Tennessee, Memphis | 30.4 | 7.0159 | 7 | 0
|  | Tennessee | Nashville | Tennessee, Nashville | 28.4 | 6.5544 | 7 | 0
TX |  | Texas | Amarillo | Texas, Amarillo | 28.4 | 6.5544 | 7 | 0
|  | Texas | Corpus Christi | Texas, Corpus Christi | 43 | 9.9238 | 10 | 0
|  | Texas | Dallas | Texas, Dallas | 34.6 | 7.9852 | 8 | 0
|  | Texas | Houston | Texas, Houston | 42 | 9.6931 | 10 | 0
|  | Texas | Lubbock | Texas, Lubbock | 30.8 | 7.1082 | 7 | 0
|  | Texas | San Antonio | Texas, San Antonio | 41.3 | 9.5315 | 10 | 0
UT |  | Utah | Salt Lake City | Utah, Salt Lake City | 19.9 | 4.5927 | 5 | 0
|  | Utah | Wendover | Utah, Wendover | 21.6 | 4.985 | 5 | 0
VT |  | Vermont | Burlington | Vermont, Burlington | 16.7 | 3.8541 | 4 | 0
VA |  | Virginia | Richmond | Virginia, Richmond | 26.8 | 6.1851 | 6 | 0
|  | Virginia | Roanoke | Virginia, Roanoke | 26.3 | 6.0697 | 6 | 0
WA |  | Washington | Seattle | Washington, Seattle | 9.4 | 2.1694 | 2 | 0
|  | Washington | Spokane | Washington, Spokane | 15.6 | 3.6003 | 4 | 0
WV |  | West Virginia | Charleston | West Virginia, Charleston | 26.1 | 6.0235 | 6 | 0
|  | West Virginia | Clarksburg | West Virginia, Clarksburg | 22.5 | 5.1927 | 5 | 0
WI |  | Wisconsin | Green Bay | Wisconsin, Green Bay | 17.5 | 4.0388 | 4 | 0
|  | Wisconsin | Madison | Wisconsin, Madison | 20.2 | 4.6619 | 5 | 0
|  | Wisconsin | Milwaukee | Wisconsin, Milwaukee | 20.9 | 4.8234 | 5 | 0
WY |  | Wyoming | Casper | Wyoming, Casper | 19.2 | 4.4311 | 4 | 0
|  | Wyoming | Cheyenne | Wyoming, Cheyenne | 18.3 | 4.2234 | 4 | 0
|  | Wyoming | Rock Springs | Wyoming, Rock Springs | 16.7 | 3.8541 | 4 | 0
AL
AR
AZ
CA
CO
CT
DC
DE
FL
GA
IA
ID
IL
IN
KS
KY
LA
MA
MD
ME
MI
MN
MO
MS
MT
NC
ND
NE
NH
NJ
NM
NV
NY
OH
OK
OR
PA
RI
SC
SD
TN
TX
UT
VA
VT
WA
WI
WV
WY
Months |  | Factor
1 |  | 12
2 |  | 6
3 |  | 4
4 |  | 3
5 |  | 2.4
6 |  | 2
7 |  | 1.7425
8 |  | 1.5
9 |  | 1.3333
10 |  | 1.2
11 |  | 1.0909
12 |  | 1

## F-Bay
Insert Logo Here
Input | System Comparison
Output
Customer Information | [6 empty] | Facility Information
Project Name:
[7 empty] | Square Footage | 10000
Contact: | [6 empty] | Annual Operating Hours | 4000
[7 empty] | Cost per kWh | 0.14
Lighting System Details | [5 empty] | Existing System |  | F-Bay System
|  |  | Select Luminaire |  |  | 400W Metal Halide High Bay |  | 2HB632 F-Bay
[6 empty] | Probe Start Metal Halide |  | T8 Fluorescent
|  |  | Quantity |  |  | 100 |  | 100
Lighting Controls |  |  | Quantity w/Lighting Controls |  |  | 0 |  | 0
|  |  | % Annual Operating Hours Controlled |  |  | 0% |  | 0%
|  |  | % Light Output Controlled |  |  | 0% |  | 0%
Energy Analysis
|  |  | Luminaire Input Watts |  |  | 455 |  | 221
|  |  | Controlled Luminaire Initial Lumens |  |  | 0 |  | 0
|  |  | Controlled Luminaire Design Lumens |  |  | #REF! |  | #REF!
|  |  | System Input Watts |  |  | 45500 |  | 22100
|  |  | System KW |  |  | 45.5 |  | 22.1
|  |  | Annual kWh |  |  | 182000 |  | 88400
|  |  | Annual Energy Costs |  |  | 25480 |  | 12376
|  |  | Annual Energy Savings ($) |  |  |  |  | 13104
|  |  | Energy Savings (%) |  |  |  |  | 51.43%
| Burned in Hours/Hours Since Last Relamp |  |  |  |  | 14000
|  |  | Lamp Life |  |  | 20000 |  | 20000
|  |  | % Depreciation |  |  | 70% |  | 40%
|  |  | Depreciation Factor |  |  | 51% |  | 95%
|  |  | S/P Ratio |  |  | 1.2247 |  | 1.3964
|  |  | Initial Lumens |  |  | 36000 |  | 18600
|  |  | Luminaire Initial Lumens |  |  | 30600 |  | 18786
|  |  | S/P Adjusted Lumens (Initial) |  |  | 37477.1931 |  | 26233.2213
|  |  | S/P Adjusted Lumens (Maintained) |  |  | 19113.3685 |  | 24921.5603
|  |  | Change in Light Output (Initial) |  |  |  |  | -30%
|  |  | Change in Light Output (Maintained) |  |  |  |  | 30.39%
|  |  | Coefficient of Utilization |  |  | 0.85 |  | 1.01
|  |  | Light Loss Factor |  |  | 1 |  | 1
|  |  | Average Footcandles (Maintained)) |  |  | 162.4636 |  | 251.7078
|  |  | Light Gain/Loss at Full Light Output (%) |  |  |  |  | 23.31%
|  |  | Lighting Power Density (LPD) |  |  | 4.55 |  | 2.21
System Costs
Per Luminaire Cost
|  |  | Total System Cost |  |  |  |  | 0
|  |  | Labor/Materials/Disposal (Lot Price) |  |  |  |  | 0
|  |  | Per Luminaire Rebate/Incentive |  |  |  |  | 0
|  |  | Total System Rebate/Incentive |  |  |  |  | 0
|  |  | Total Contract Price |  |  |  |  | 0
Payback Analysis
|  |  | Simple Payback |  |  |  |  | 0
|  |  | IRR (%) |  |  |  |  | #DIV/0!
Light level calculations are based on scotopic/photopic adjusted lumen values. This is only an estimate. Cooper Lighting's online zonal cavity calulators and lighting layout software and services should be used for a final evaluation.
Click here for more information on Cooper Lighting's full offering of industrial energy efficient fluorescent luminaires.
Return to TOP
Return to HOME |  |  | Annual Energy Costs |  |  |  |  | Average Footcandles (Maintained))
| 400W Metal Halide High Bay |  | 25480 |  |  |  | 400W Metal Halide High Bay | 162.4636
| 2HB632 F-Bay |  | 12376 |  |  |  | 2HB632 F-Bay | 251.7078
|  | Initial lmns | Design lmns | S/P Adjusted Initial lmns | S/P Adjusted Maintained lmns
| 400W Metal Halide High Bay | 36000 | #REF! | 37477.1931 | 19113.3685
| 2HB632 F-Bay | 18600 | #REF! | 26233.2213 | 24921.5603
System | 2HB632 F-Bay |  | 400W Metal Halide High Bay
Input Watts | 221 |  | 455
Footcandles | 251.7078 |  | 162.4636
Please Select | Input Watts | Initial Lumens | Design Lumens | bf | LLF | CU | S/P | Adj S/P | Lamp Life
150W High Pressure Sodium High Bay | 188 | 16000 | 14400 |  | 0.68 | 0.85 | 0.62 | 0.7874 | 24000 | High Pressure Sodium
250W High Pressure Sodium High Bay | 300 | 30000 | 19800 |  | 0.68 | 0.85 | 0.62 | 0.7874 | 24000 | High Pressure Sodium
400W High Pressure Sodium High Bay | 464 | 51000 | 29288 |  | 0.68 | 0.85 | 0.62 | 0.7874 | 24000 | High Pressure Sodium
1000W High Pressure Sodium High Bay | 1100 | 130000 | 126000 |  | 0.68 | 0.85 | 0.62 | 0.7874 | 24000 | High Pressure Sodium
175W Metal Halide High Bay | 213 | 13600 | 8800 |  | 0.68 | 0.85 | 1.5 | 1.2247 | 10000 | Probe Start Metal Halide
250W Metal Halide High Bay | 295 | 20800 | 13500 |  | 0.68 | 0.85 | 1.5 | 1.2247 | 10000 | Probe Start Metal Halide
400W Metal Halide High Bay | 455 | 36000 | 16307 |  | 0.68 | 0.85 | 1.5 | 1.2247 | 20000 | Probe Start Metal Halide
1000W Metal Halide High Bay | 1085 | 102800 | 79000 |  | 0.68 | 0.85 | 1.5 | 1.2247 | 15000 | Probe Start Metal Halide
150W PSMH High Bay | 189 | 13300 | 10000 |  | 0.81 | 0.9 | 1.5 | 1.2247 | 15000 | Pulse Start Metal Halide
175W PSMH High Bay | 208 | 17500 | 13000 |  | 0.81 | 0.9 | 1.5 | 1.2247 | 15000 | Pulse Start Metal Halide
250W PSMH High Bay | 291 | 23000 | 17000 |  | 0.81 | 0.9 | 1.5 | 1.2247 | 20000 | Pulse Start Metal Halide
320W PSMH High Bay | 368 | 32000 | 22500 |  | 0.81 | 0.9 | 1.5 | 1.2247 | 20000 | Pulse Start Metal Halide
350W PSMH High Bay | 400 | 36500 | 27000 |  | 0.81 | 0.9 | 1.5 | 1.2247 | 20000 | Pulse Start Metal Halide
450W PSMH High Bay | 404 | 44000 | 35000 |  | 0.81 | 0.9 | 1.5 | 1.2247 | 20000 | Pulse Start Metal Halide
750W PSMH High Bay | 820 | 82000 | 60000 |  | 0.81 | 0.9 | 1.5 | 1.2247 | 16000 | Pulse Start Metal Halide
1000W PSMH High Bay | 1080 | 115000 | 90000 |  | 0.81 | 0.9 | 1.5 | 1.2247 | 12000 | Pulse Start Metal Halide
(2) 34W T12 Magnetic Industrial | 80 | 5600 | 5200 |  | 0.792 | 0.88 | 1.8 | 1.3416 | 20000 | T12 Fluorescent
(3) 34W T12 Magnetic Industrial | 130 | 8400 | 7800 |  | 0.792 | 0.88 | 1.8 | 1.3416 | 20000 | T12 Fluorescent
(4) 34W T12 Magnetic Industrial | 160 | 11200 | 10400 |  | 0.792 | 0.88 | 1.8 | 1.3416 | 20000 | T12 Fluorescent
(2) 110W T12 HO Magnetic Industrial | 253 | 18400 | 16560 |  | 0.792 | 0.88 | 1.8 | 1.3416 | 12000 | T12 Fluorescent
(3) 110W T12 HO Magnetic Industrial | 398 | 27600 | 24840 |  | 0.792 | 0.88 | 1.8 | 1.3416 | 12000 | T12 Fluorescent
(4) 110W T12 HO Magnetic Industrial | 506 | 36800 | 33120 |  | 0.792 | 0.88 | 1.8 | 1.3416 | 12000 | T12 Fluorescent
150W PSMH ECON | 189 | 13300 | 10000 |  | 0.8883 | 0.9 | 1.5 | 1.2247 | 15000 | Electronic Pulse Start Metal Halide
175W PSMH ECON | 194 | 17500 | 13000 |  | 0.8883 | 0.9 | 1.5 | 1.2247 | 15000 | Electronic Pulse Start Metal Halide
250W PSMH ECON | 269 | 23000 | 18344.34 |  | 0.8883 | 0.9 | 1.5 | 1.2247 | 30000 | Electronic Pulse Start Metal Halide
320W PSMH ECON | 345 | 30000 | 23927.4 |  | 0.8883 | 0.9 | 1.5 | 1.2247 | 30000 | Electronic Pulse Start Metal Halide
350W PSMH ECON | 375 | 34000 | 27117.72 |  | 0.8883 | 0.9 | 1.5 | 1.2247 | 30000 | Electronic Pulse Start Metal Halide
400W PSMH ECON | 426 | 40000 | 32000 |  | 0.8883 | 0.9 | 1.5 | 1.2247 | 30000 | Electronic Pulse Start Metal Halide
Please Select
HB432 F-Bay | 147 | 12400 | 11800 |  | 0.9876 | 1.01 | 1.95 | 1.3964 | 20000 | T8 Fluorescent
HB454 F-Bay | 229 | 20000 | 17800 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
2HB632 F-Bay | 221 | 18600 | 17700 |  | 0.9876 | 1.01 | 1.95 | 1.3964 | 20000 | T8 Fluorescent
2HB654 F-Bay | 346 | 20000 | 26700 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
I8232 F-Bay | 73 | 6200 | 5900 |  | 0.9876 | 1.01 | 1.95 | 1.3964 | 20000 | T8 Fluorescent
I8332 F-Bay | 109 | 9300 | 8850 |  | 0.9876 | 1.01 | 1.95 | 1.3964 | 20000 | T8 Fluorescent
I8432 F-Bay | 147 | 12400 | 11800 |  | 0.9876 | 1.01 | 1.95 | 1.3964 | 20000 | T8 Fluorescent
I5254 F-Bay | 117 | 10000 | 8900 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
I5354 F-Bay | 182 | 15000 | 13350 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
I5454 F-Bay | 229 | 20000 | 17800 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
8TI5254 F-Bay | 229 | 20000 | 17800 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
8TI5354 F-Bay | 346 | 30000 | 26700 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
8TI5454 F-Bay | 458 | 40000 | 35600 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
3HBO832 F-Bay | 302 | 24800 | 23600 |  | 0.9876 | 1.01 | 1.95 | 1.3964 | 20000 | T8 Fluorescent
3HBO854 F-Bay | 458 | 40000 | 35600 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
MB132 Micro Bay | 46 | 3100 | 2950 |  | 0.9876 | 1.01 | 1.95 | 1.3964 | 20000 | T8 Fluorescent
MB232 Micro Bay | 73 | 6200 | 5900 |  | 0.9876 | 1.01 | 1.95 | 1.3964 | 20000 | T8 Fluorescent
MB154 Micro Bay | 62 | 5000 | 4450 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
MB254 Micro Bay | 117 | 10000 | 8900 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
8TMB132 Micro Bay | 73 | 6200 | 5900 |  | 0.9876 | 1.01 | 1.95 | 1.3964 | 20000 | T8 Fluorescent
8TMB232 Micro Bay | 147 | 12400 | 11800 |  | 0.9876 | 1.01 | 1.95 | 1.3964 | 20000 | T8 Fluorescent
8TMB154 Micro Bay | 117 | 10000 | 8900 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
8TMB254 Micro Bay | 229 | 20000 | 17800 |  | 0.855 | 1.01 | 1.9 | 1.3784 | 30000 | T5HO Fluorescent
Please Select |  | Please Select
0% |  | 100%
10% |  | 90% | [6 empty] | v
20% |  | 80%
30% |  | 70%
40% |  | 60%
50% |  | 50%
60% |  | 40%
70% |  | 30%
80% |  | 20%
90% |  | 10%
100% |  | 0%
|  |  | System | Percent Output | Combo | Depreciation Factor
|  |  | T8 Fluorescent | 0% | T8 Fluorescent-0 | 100 | 100%
|  |  | T8 Fluorescent | 10% | T8 Fluorescent-0.1 | 98 | 98%
|  |  | T8 Fluorescent | 20% | T8 Fluorescent-0.2 | 96 | 96%
|  |  | T8 Fluorescent | 30% | T8 Fluorescent-0.3 | 95.5 | 95.5%
|  |  | T8 Fluorescent | 40% | T8 Fluorescent-0.4 | 95 | 95%
|  |  | T8 Fluorescent | 50% | T8 Fluorescent-0.5 | 94.5 | 94.5%
|  |  | T8 Fluorescent | 60% | T8 Fluorescent-0.6 | 94 | 94%
|  |  | T8 Fluorescent | 70% | T8 Fluorescent-0.7 | 93.5 | 93.5%
|  |  | T8 Fluorescent | 80% | T8 Fluorescent-0.8 | 93 | 93%
|  |  | T8 Fluorescent | 90% | T8 Fluorescent-0.9 | 92.5 | 92.5%
|  |  | T8 Fluorescent | 100% | T8 Fluorescent-1 | 92 | 92%
|  |  | T5HO Fluorescent | 0% | T5HO Fluorescent-0 | 100 | 100%
|  |  | T5HO Fluorescent | 10% | T5HO Fluorescent-0.1 | 98 | 98%
|  |  | T5HO Fluorescent | 20% | T5HO Fluorescent-0.2 | 96 | 96%
|  |  | T5HO Fluorescent | 30% | T5HO Fluorescent-0.3 | 95 | 95%
|  |  | T5HO Fluorescent | 40% | T5HO Fluorescent-0.4 | 94 | 94%
|  |  | T5HO Fluorescent | 50% | T5HO Fluorescent-0.5 | 93 | 93%
|  |  | T5HO Fluorescent | 60% | T5HO Fluorescent-0.6 | 92 | 92%
|  |  | T5HO Fluorescent | 70% | T5HO Fluorescent-0.7 | 91.5 | 91.5%
|  |  | T5HO Fluorescent | 80% | T5HO Fluorescent-0.8 | 91 | 91%
|  |  | T5HO Fluorescent | 90% | T5HO Fluorescent-0.9 | 90.5 | 90.5%
|  |  | T5HO Fluorescent | 100% | T5HO Fluorescent-1 | 90 | 90%
|  |  | T12 Fluorescent | 0% | T12 Fluorescent-0 | 100 | 100%
|  |  | T12 Fluorescent | 10% | T12 Fluorescent-0.1 | 95 | 95%
|  |  | T12 Fluorescent | 20% | T12 Fluorescent-0.2 | 91 | 91%
|  |  | T12 Fluorescent | 30% | T12 Fluorescent-0.3 | 87 | 87%
|  |  | T12 Fluorescent | 40% | T12 Fluorescent-0.4 | 85 | 85%
|  |  | T12 Fluorescent | 50% | T12 Fluorescent-0.5 | 81 | 81%
|  |  | T12 Fluorescent | 60% | T12 Fluorescent-0.6 | 79 | 79%
|  |  | T12 Fluorescent | 70% | T12 Fluorescent-0.7 | 77.5 | 77.5%
|  |  | T12 Fluorescent | 80% | T12 Fluorescent-0.8 | 76 | 76%
|  |  | T8 Fluorescent | 90% | T8 Fluorescent-0.9 | 75 | 75%
|  |  | T5HO Fluorescent | 100% | T5HO Fluorescent-1 | 74 | 74%
|  |  | T5HO Fluorescent | 0% | T5HO Fluorescent-0 | 100 | 100%
|  |  | High Pressure Sodium | 10% | High Pressure Sodium-0.1 | 97 | 97%
|  |  | High Pressure Sodium | 20% | High Pressure Sodium-0.2 | 95 | 95%
|  |  | High Pressure Sodium | 30% | High Pressure Sodium-0.3 | 93 | 93%
|  |  | High Pressure Sodium | 40% | High Pressure Sodium-0.4 | 91 | 91%
|  |  | High Pressure Sodium | 50% | High Pressure Sodium-0.5 | 87 | 87%
|  |  | High Pressure Sodium | 60% | High Pressure Sodium-0.6 | 85 | 85%
|  |  | High Pressure Sodium | 70% | High Pressure Sodium-0.7 | 81 | 81%
|  |  | High Pressure Sodium | 80% | High Pressure Sodium-0.8 | 77 | 77%
|  |  | High Pressure Sodium | 90% | High Pressure Sodium-0.9 | 74 | 74%
|  |  | High Pressure Sodium | 100% | High Pressure Sodium-1 | 70 | 70%
|  |  | Probe Start Metal Halide | 0% | Probe Start Metal Halide-0 | 100 | 100%
|  |  | Probe Start Metal Halide | 10% | Probe Start Metal Halide-0.1 | 89 | 89%
|  |  | Probe Start Metal Halide | 20% | Probe Start Metal Halide-0.2 | 79 | 79%
|  |  | Probe Start Metal Halide | 30% | Probe Start Metal Halide-0.3 | 72 | 72%
|  |  | Probe Start Metal Halide | 40% | Probe Start Metal Halide-0.4 | 64 | 64%
|  |  | Probe Start Metal Halide | 50% | Probe Start Metal Halide-0.5 | 58 | 58%
|  |  | Probe Start Metal Halide | 60% | Probe Start Metal Halide-0.6 | 54 | 54%
|  |  | Probe Start Metal Halide | 70% | Probe Start Metal Halide-0.7 | 51 | 51%
|  |  | Probe Start Metal Halide | 80% | Probe Start Metal Halide-0.8 | 48 | 48%
|  |  | Probe Start Metal Halide | 90% | Probe Start Metal Halide-0.9 | 44 | 44%
|  |  | Probe Start Metal Halide | 100% | Probe Start Metal Halide-1 | 41 | 41%
|  |  | Pulse Start Metal Halide | 0% | Pulse Start Metal Halide-0 | 100 | 100%
|  |  | Pulse Start Metal Halide | 10% | Pulse Start Metal Halide-0.1 | 93 | 93%
|  |  | Pulse Start Metal Halide | 20% | Pulse Start Metal Halide-0.2 | 86 | 86%
|  |  | Pulse Start Metal Halide | 30% | Pulse Start Metal Halide-0.3 | 79 | 79%
|  |  | Pulse Start Metal Halide | 40% | Pulse Start Metal Halide-0.4 | 75 | 75%
|  |  | Pulse Start Metal Halide | 50% | Pulse Start Metal Halide-0.5 | 71 | 71%
|  |  | Pulse Start Metal Halide | 60% | Pulse Start Metal Halide-0.6 | 69 | 69%
|  |  | Pulse Start Metal Halide | 70% | Pulse Start Metal Halide-0.7 | 65 | 65%
|  |  | Pulse Start Metal Halide | 80% | Pulse Start Metal Halide-0.8 | 63 | 63%
|  |  | Pulse Start Metal Halide | 90% | Pulse Start Metal Halide-0.9 | 60 | 60%
|  |  | Pulse Start Metal Halide | 100% | Pulse Start Metal Halide-1 | 58 | 58%
|  |  | Electronic Pulse Start Metal Halide | 0% | Electronic Pulse Start Metal Halide-0 | 100 | 100%
|  |  | Electronic Pulse Start Metal Halide | 10% | Electronic Pulse Start Metal Halide-0.1 | 94 | 94%
|  |  | Electronic Pulse Start Metal Halide | 20% | Electronic Pulse Start Metal Halide-0.2 | 90 | 90%
|  |  | Electronic Pulse Start Metal Halide | 30% | Electronic Pulse Start Metal Halide-0.3 | 88 | 88%
|  |  | Electronic Pulse Start Metal Halide | 40% | Electronic Pulse Start Metal Halide-0.4 | 86 | 86%
|  |  | Electronic Pulse Start Metal Halide | 50% | Electronic Pulse Start Metal Halide-0.5 | 85 | 85%
|  |  | Electronic Pulse Start Metal Halide | 60% | Electronic Pulse Start Metal Halide-0.6 | 84 | 84%
|  |  | Electronic Pulse Start Metal Halide | 70% | Electronic Pulse Start Metal Halide-0.7 | 83 | 83%
|  |  | Electronic Pulse Start Metal Halide | 80% | Electronic Pulse Start Metal Halide-0.8 | 82 | 82%
|  |  | Electronic Pulse Start Metal Halide | 90% | Electronic Pulse Start Metal Halide-0.9 | 81 | 81%
|  |  | Electronic Pulse Start Metal Halide | 100% | Electronic Pulse Start Metal Halide-1 | 80 | 80%
Note on C37: This number is factored against the individual lamp source life and lumen depreciation curve. It is not an indication of selected sources true lamp life.
Note on E19: If there are controls on the system enter the quantity of luminaires equipped with the controls. If there are no controls, field should have a zero.
Note on E20: Enter the percent of time (operating hours) the luminaires are controlled. For example, if the luminaires are equipped with an occupancy sensor it might only be triggered 50%. If it is a high traffic area then the percentage would be higher and vice versa.
Note on E21: Enter the percent of light output of the luminaires when they are controlled. For example, if the luminaires are equipped with an occupancy sensor this is the percentage of the light output when the luminaires are not illuminated.
Note on E49: Maintained Illuminance is factored with Scotopic/Photopic adjusted lumen values. The Proposed System is based on 40% of rated life. Based on full light output.

## Stair-Lite
Insert Logo Here
Stair-Lite 2 Annual Savings Calculator
Input
Output
Customer Information |  |  |  | Facility Information
Project Name: |  |  |  | Annual Operating Hours
|  |  |  | % Per Day Space is Occupied | 5% | 0
Contact: |  |  |  | Cost Per kWh
Lighting System Details |  |  | Existing |  | Stair-Lite 2
Number of Stairwells
Number of Luminaires Per Stairwell
|  | Input Watts Per Luminaire |  |  | 71 | 0
|  | Input Watts when Unoccupied | - |  | 42 | 0
|  | System kW | 0 |  | 0 | 0
|  | Annual kW Saved |  |  | 0
|  | Annual kWh Saved |  |  | 0
For more information on the energy efficient Stair-Lite 2 product offering, click here.
Return to HOME
Note on I9: Average Stairwells are occupied less than 5% per 24 hour day.

## Audit Tips
Insert Logo Here |  | Tips for a Successful Audit
Starting with a plan for any lighting upgrade is a necessity. Retrofits are time consuming and potentially costly if not implemented correctly the first time. A crucial step in the success of any upgrade is an audit of the existing lighting system - a comprehensive review of the current fixtures, environment, and operating conditions.
· Best way to start is with building drawings and floor plans including any remodeling and locations of HVAC, controls, zones, exits, equipment rooms, etc. If drawings are not readily available, ask for the emergency exit plans posted on each floor or sketch the room, floor, or building on graph paper.
· Bring a digital camera. It’s invaluable in capturing nuances in the fixtures and application – dirty windows, sprinkler systems, structural obstructions, and other obstructions that might inhibit installation of a retrofit or affect the lighting levels of the existing fixtures.
Do you have what you need to get started?
Names of the Key Contacts
Lightmeter
| · Utilities have a number of service plans and charges. So ask for two years of utility bills and only settle with at least summer and winter months. The most extreme seasons help to capture the demand variations as well as peak demand charges, taxes, surcharges and other miscellaneous utility expenditures. |  |  | Audit forms
Clipboard
Graph Paper
Digital Camera
Laser/Tape Measurer
| · Use a lightmeter to determine the light levels (footcandles, FC) of the application taking into account obstructions or spill light from windows or skylights. |  |  | Occupancy/Timer Logger
Business Cards
· Capture all of the fixtures in the space; looking for task lighting, recessed, and emergency lighting.
· Get up on a ladder. Get in the maintenance closet. Look at the lamps and ballasts up close to make sure you’ve got the right information.
· Are the fixtures open or enclosed, equipped with wireguards, wired for emergency ballasts or even remote mount ballasts?
· Have any burned out lamps or failed ballast been factored into the light levels? When was the last maintenance?
Do you have what you need to leave the job site?
| · With a broad range of controls from daylighting, timers, and occupancy sensors available, it is important to note the type and part number and take a picture of the control and any visible settings. |  |  | Complete Audit Form
Utility Bills (Summer & Winter Months)
| · A light logger control will help determine when the space is occupied or vacant and when the lights are on or off. Note whether the systems are on/off or simply dimmed. If dimmed note the % dimmed as well as the % of time dimmed. |  |  | Building/Floor/Room Drawings
Pictures of Fixtures, Obstructions, etc
Audits are fact finding missions. With the wrong facts, the project’s payback analysis will under or, worse, over-state the benefits of the upgrade. Make sure you set realistic expectations with a sound and accurate audit.
Return to TOP
Return to HOME

## Audit Site Background (1)
Site Background
FACILITY INFORMATION
Company Name
Facility Name
Street Address
City, State & Zip
Primary Facility Function
Serving Electrical Utility |  | Total Square Footage | sq. ft.
$/kWh Energy Rate |  | % Production | %
Rebates Available (circle one) | Yes No Not Sure | % Warehouse | %
EPAct Qualified (circle one) | Yes No Not Sure | % Office | %
|  | % Other | %
Lighting Plans Available (circle one) | Yes No Not Sure | Total | %
Preferred Maintenance Contractor
Assumed Maintenance Labor Rate | $
CUSTOMER INFORMATION
Contact Full Name
Title
Phone #
E-Mail
Customer Identified Goals | Circle One Below | Corporate Return Requirements
Energy Savings | High Medium Low | Simple Payback (Years)
Maintenance Savings | High Medium Low | Return on Investment | %
Light Level Improvement (FC) | High Medium Low | Annual Cash Flow | $
Light Quality Improvement (CRI) | High Medium Low
Other Goals
High Medium Low
High Medium Low
Other Relevant Information
Cooper Lighting 1121 Highway 74 South, Peachtree City, GA 30269 www.cooperenergysolutions.com energysolutions@cooperlighting.com
Return to TOP
Return to HOME

## Audit Fixture Information (2)
Fixture Information
Company |  |  |  | Contact Name
Facility Name
Address
Area Description
Fixture ID #
Fixture Description
# Lamps | Lamp Type | Ballast Type | Voltage
Proposed Fixture
Comments
Area Description
Fixture ID #
Fixture Description
# Lamps | Lamp Type | Ballast Type | Voltage
Proposed Fixture
Comments
Area Description
Fixture ID #
Fixture Description
# Lamps | Lamp Type | Ballast Type | Voltage
Proposed Fixture
Comments
Area Description
Fixture ID #
Fixture Description
# Lamps | Lamp Type | Ballast Type | Voltage
Proposed Fixture
Comments
Cooper Lighting 1121 Highway 74 South, Peachtree City, GA 30269 www.cooperenergysolutions.com energysolutions@cooperlighting.com
Return to TOP
Return to HOME

## Audit Detail - Fixture (3)
Audit Detail
Fixture Information
Location Description | Fixture Type | Fixture Qty | Hours/ Year | Mounting Height | Avg. FC | Comments
Cooper Lighting 1121 Highway 74 South, Peachtree City, GA 30269 www.cooperenergysolutions.com energysolutions@cooperlighting.com
Return to TOP
Return to HOME

## Sheet2 (hidden)
Series Name | Comparison System | Catalog Number | Energy Savings | Light Output | Mounting Height | Lamp Replacement Selection | High Temp | Motion Sensor | Mounting Height | Comparison System | High Temp | Motion Sensor | Lamp Replacement Selection | Series Name | Comparison System | Catalog Number | Energy Savings | Light Output | Mounting Height | Lamp Replacement Selection | High Temp | Motion Sensor | Mounting Height | Comparison System | High Temp | Motion Sensor | Lamp Replacement Selection | Series Name | Comparison System | Catalog Number | Energy Savings | Light Output | Mounting Height | Lamp Replacement Selection | High Temp | Motion Sensor
2HBG Series | 250W HPS | 2HBG-432-ER8/PLUS | 68% | -33.37% | 20' | T8 | No | Yes | 20' | 250W HPS | No | No | T8 | 2HBHD Series | 250W HPS | 2HBHD-432-CL-EB8/PLUS | 51% | -1.77% | 20' | T8 | No | No | 20' | 250W HPS | No | Yes | T5 | 2HBG Series | 250W HPS | 2HBG-454 | 51% | 2.625% | 20' | T5 | No | Yes
2HBG Series | 250W HPS | 2HBG-454 | 51% | 2.625% | 20' | T5 | No | Yes | [5 empty] | HB Series | 250W HPS | HB-332-EB8/PLUS | 64% | -20% | 20' | T8 | No | No | [5 empty] | 2HBHD Series | 250W HPS | 2HBHD-454 | 24% | 4.35% | 20' | T5 | No | Yes
2HBHD Series | 250W HPS | 2HBHD-432-CL-EB8/PLUS | 51% | -1.77% | 20' | T8 | No | No | [5 empty] | I5/I8 Series | 250W HPS | I8-332-EB8/PLUS | 78% | -13.24% | 20' | T8 | No | No | [5 empty] | HB Series | 250W HPS | HB-354T5 | 39% | 16.35% | 20' | T5 | No | Yes
2HBHD Series | 250W HPS | 2HBHD-432-CL-ER8/PLUS | 51% | -1.77% | 20' | T8 | No | Yes
2HBHD Series | 250W HPS | 2HBHD-454 | 24% | 4.35% | 20' | T5 | No | Yes
HB Series | 250W HPS | HB-332-EB8/PLUS | 64% | -20% | 20' | T8 | No | No
HB Series | 250W HPS | HB-332-ER8/PLUS | 64% | -20% | 20' | T8 | No | Yes
HB Series | 250W HPS | HB-354T5 | 39% | 16.35% | 20' | T5 | No | Yes
I5/I8 Series | 250W HPS | I8-332-EB8/PLUS | 78% | -13.24% | 20' | T8 | No | No
2HBG Series | 250W MH | 2HBG-432-EB8/PLUS | 68% | -33.37% | 20' | T8 | No | No
2HBG Series | 250W MH | 2HBG-454 | 50% | 2.625% | 20' | T5 | No | Yes
2HBHD Series | 250W MH | 2HBHD-432-CL-EB8/PLUS | 50% | 21.41% | 20' | T8 | No | No
2HBHD Series | 250W MH | 2HBHD-432-CL-ER8/PLUS | 50% | 21.41% | 20' | T8 | No | Yes
2HBHD Series | 250W MH | 2HBHD-454 | 22% | 26.14% | 20' | T5 | No | Yes
HB Series | 250W MH | HB-332-EB8/PLUS | 63% | 8% | 20' | T8 | No | No
HB Series | 250W MH | HB-332-ER8/PLUS | 63% | 8% | 20' | T8 | No | Yes
HB Series | 250W MH | HB-354T5 | 38% | 35.4% | 20' | T5 | No | Yes
I5/I8 Series | 250W MH | I8-332-EB8/PLUS | 66% | 12.56% | 20' | T8 | No | No
Arctic Bay Series | 400W HPS | 2AB-454-UNV-EBT1 | 51% | -21% | 20' | T5 | No | Yes
Arctic Bay Series | 400W MH | 2AB-454-UNV-EBT1 | 50% | 3% | 20' | T5 | No | Yes
2HB Series | 400W HPS | 2HB632 | 53.02% | 0.332% | 30' | T8 | No | No
2HB Series | 400W MH | 2HB632 | 52.09% | 20.08% | 30' | T8 | No | No
2HB Series | 400W HPS | 2HB632PS | 53.02% | 0.332% | 30' | T8 | No | Yes
2HB Series | 400W MH | 2HB632PS | 52.09% | 20.08% | 30' | T8 | No | Yes
2HB Series | 400W HPS | 2HB654HT5 | 21.77% | 30.29% | 30' | T5 | Yes | Yes
2HB Series | 400W MH | 2HB654HT5 | 20.22% | 44.1% | 30' | T5 | Yes | Yes
2HB Series | 400W HPS | 2HB654T5 | 21.77% | 30.29% | 30' | T5 | No | Yes
2HB Series | 400W MH | 2HB654T5 | 20.22% | 44.1% | 30' | T5 | No | Yes
2HBG Series | 400W HPS | 2HBG-632-EB8/PLUS | 51.21% | 11.08% | 30' | T8 | No | No
2HBG Series | 400W MH | 2HBG-632-EB8/PLUS | 51.21% | 11.08% | 30' | T8 | No | No
2HBG Series | 400W HPS | 2HBG-632-ER8/PLUS | 51.21% | 11.08% | 30' | T8 | No | Yes
2HBG Series | 400W MH | 2HBG-632-ER8/PLUS | 51.21% | 11.08% | 30' | T8 | No | Yes
2HBG Series | 400W HPS | 2HBG-654 | 25% | 35.08% | 30' | T5 | No | Yes
2HBG Series | 400W MH | 2HBG-654 | 24% | 35.08% | 30' | T5 | No | Yes
2HBHD Series | 400W HPS | 2HBHD-632-CL-EB8/PLUS | 52.16% | -13.08% | 30' | T8 | No | No
2HBHD Series | 400W MH | 2HBHD-632-CL-EB8/PLUS | 51.21% | 9.322% | 30' | T8 | No | No
2HBHD Series | 400W HPS | 2HBHD-632-CL-ER8/PLUS | 52.16% | -13.08% | 30' | T8 | No | Yes
2HBHD Series | 400W MH | 2HBHD-632-CL-ER8/PLUS | 51.21% | 9.322% | 30' | T8 | No | Yes
2HBHD Series | 400W HPS | 2HBHD-654 | 25% | -6.278% | 30' | T5 | No | Yes
2HBHD Series | 400W MH | 2HBHD-654 | 24% | 14.77% | 30' | T5 | No | Yes
Arctic Bay Series | 400W HPS | 2AB-654-UNV-EBT2 | 25% | 19% | 30' | T5 | No | Yes
Arctic Bay Series | 400W MH | 2AB-654-UNV-EBT2 | 24% | 35% | 30' | T5 | No | Yes
HB Series | 400W HPS | HB432 | 68% | -49.5% | 30' | T8 | No | No
HB Series | 400W MH | HB432 | 67% | -19.89% | 30' | T8 | No | No
HB Series | 400W HPS | HB432PS | 68% | -49.5% | 30' | T8 | No | Yes
HB Series | 400W MH | HB432PS | 67% | -19.89% | 30' | T8 | No | Yes
HB Series | 400W HPS | HB454HT5 | 50% | -3.785% | 30' | T5 | Yes | Yes
HB Series | 400W MH | HB454HT5 | 49% | 16.77% | 30' | T5 | Yes | Yes
HB Series | 400W HPS | HB454T5 | 50% | -3.785% | 30' | T5 | No | Yes
HB Series | 400W MH | HB454T5 | 49% | 16.77% | 30' | T5 | No | Yes
I5/I8 Series | 1000W HPS | 8I5355 | 25% | 31% | 30' | T5 | No | Yes
I5/I8 Series | 1000W MH | 8I5355 | 24% | 45% | 30' | T5 | No | Yes
I5/I8 Series | 250W HPS | I5355 | 39% | 17.32% | 30' | T5 | No | Yes
I5/I8 Series | 250W MH | I5355 | 38% | 36.16% | 30' | T5 | No | Yes
I5/I8 Series | 400W HPS | I8-432-EB8/PLUS | 51% | -13.51% | 30' | T8 | No | No
I5/I8 Series | 400W MH | I8-432-EB8/PLUS | 51% | 15.07% | 30' | T8 | No | No
I5/I8 Series | 400W HPS | I8-432-ER8/PLUS | 51% | -13.51% | 30' | T8 | No | Yes
I5/I8 Series | 400W MH | I8-432-ER8/PLUS | 51% | 15.07% | 30' | T8 | No | Yes
3HBO Series | 1000W HPS | 3HBO-832-EB/PLUS | 72.55% | 4.3% | 40' | T8 | Yes | No
3HBO Series | 1000W MH | 3HBO-832-EB/PLUS | 72.17% | -17.71% | 40' | T8 | Yes | No
3HBO Series | 1000W HPS | 3HBO-832-ER/PLUS | 72.55% | 4.3% | 40' | T8 | Yes | Yes
3HBO Series | 1000W MH | 3HBO-832-ER/PLUS | 72.17% | -17.71% | 40' | T8 | Yes | Yes
3HBO Series | 1000W HPS | 3HBO-854 | 57.64% | 30.13% | 40' | T5 | Yes | Yes
3HBO Series | 1000W MH | 3HBO-854 | 58% | 14.06% | 40' | T5 | Yes | Yes
3HBO Series | 1000W HPS | 3HBO-832-EB/PLUS | 72.55% | 4.3% | 40' | T8 | No | No
3HBO Series | 1000W MH | 3HBO-832-EB/PLUS | 72.17% | -17.71% | 40' | T8 | No | No
3HBO Series | 1000W HPS | 3HBO-832-ER/PLUS | 72.55% | 4.3% | 40' | T8 | No | Yes
3HBO Series | 1000W MH | 3HBO-832-ER/PLUS | 72.17% | -17.71% | 40' | T8 | No | Yes
3HBO Series | 1000W HPS | 3HBO-854 | 57.64% | 30.13% | 40' | T5 | No | Yes
3HBO Series | 1000W MH | 3HBO-854 | 58% | 14.06% | 40' | T5 | No | Yes
I5/I8 Series | 400W HPS | I5455 | 52% | -4.455% | 30' | T5 | No | Yes
I5/I8 Series | 400W MH | I5455 | 50% | 16.24% | 30' | T5 | No | Yes
I5/I8 Series | 1000W HPS | 8T18-454T5 | 57.64% | 25.62% | 40' | T5 | No | Yes
I5/I8 Series | 1000W MH | 8T18-454T5 | 58% | 8.51% | 40' | T5 | No | Yes
I5/I8 Series | 1000W HPS | 8TI8-432-EB8/PLUS | 58% | 26% | 40' | T8 | No | No
I5/I8 Series | 1000W MH | 8TI8-432-EB8/PLUS | 58% | 9% | 40' | T8 | No | No
I5/I8 Series | 1000W HPS | 8TI8-432-ER8/PLUS | 58% | 26% | 40' | T8 | No | Yes
I5/I8 Series | 1000W MH | 8TI8-432-ER8/PLUS | 58% | 9% | 40' | T8 | No | Yes
MicroBay Series | (1) 96" T12HO Strip | 8TMB-232-FB-EB81 | 61.38% | 37.2% | 30' | T8 | No | No
MicroBay Series | (2) 34W T12 Strip | 8TMB-232-FB-EB81 | 55.56% | 37.9% | 30' | T8 | No | No
MicroBay Series | (1) 96" T12HO Strip | 8TMB-232-FB-ER81 | 61.38% | 37.2% | 30' | T8 | No | No
MicroBay Series | (2) 34W T12 Strip | 8TMB-232-FB-ER81 | 55.56% | 37.9% | 30' | T8 | No | No
MicroBay Series | (1) 96" T12HO Strip | MB-154-FB | 55.17% | 22.47% | 30' | T5 | No | Yes
MicroBay Series | (2) 34W T12 Strip | MB-154-FB | 48.41% | 23.33% | 30' | T5 | No | Yes
MicroBay Series | (1) 96" T12HO Strip | MB-232-FB-EB81 | 61.38% | 37.27% | 30' | T8 | No | No
MicroBay Series | (2) 34W T12 Strip | MB-232-FB-EB81 | 55.56% | 37.96% | 30' | T8 | No | No
MicroBay Series | (1) 96" T12HO Strip | MB-232-FB-ER81 | 61.38% | 37.27% | 30' | T8 | No | Yes
MicroBay Series | (2) 34W T12 Strip | MB-232-FB-ER81 | 55.56% | 37.96% | 30' | T8 | No | Yes
MicroBay Series | 400W MH | (3) 8TMB-132-FB-EB81 | 4% | 14% | 30' | T8 | No | No
MicroBay Series | 400W HPS | (3) 8TMB-132-FB-EB81 | 6% | -7% | 30' | T8 | No | No
MicroBay Series | 400W MH | (3) 8TMB-132-FB-ER81 | 4% | 14% | 30' | T8 | No | Yes
MicroBay Series | 400W HPS | (3) 8TMB-132-FB-ER81 | 6% | -7% | 30' | T8 | No | Yes
MicroBay Series | 400W MH | (2) 8TMB-154-FB | -3% | 20% | 30' | T5 | No | Yes
MicroBay Series | 400W HPS | (2) 8TMB-154-FB | 1% | 1% | 30' | T5 | No | Yes

## LuminaireSelector
Insert Logo Here
Retrofit Luminaire Selector
Input
Output
Customer Information
Project Name:
Contact:
Existing Fixture Characteristics
|  |  |  | Mounting Height | 20'
|  |  |  | Select Existing Fixture Wattage & Source | 250W HPS
|  |  |  | High Temperature Environment | No
|  |  |  | For Use with Motion Sensor | No
|  | T5 Part Number | Energy Savings | Light Output | T8 Part Number | Energy Savings | Light Output
| HB Series | HB-354T5 | 39% | 16.35% | HB-332-EB8/PLUS | 64% | -20%
2HB Series
| I5/I8 Series |  |  |  | I8-332-EB8/PLUS | 78% | -13.24%
3HBO Series
| 2HBG Series | 2HBG-454 | 51% | 2.625%
MicroBay Series
Note: These are estimated savings only. These annual and monthly savings are based on a number of variables and assumptions that could change over time. The actual savings derived by your firm may be higher or lower.
Return to HOME
Please Select | Please Select | Please Select |  | Please Select
Yes | T5 | 20' |  | 250W MH
No | T8 | 30' |  | 250W HPS
|  | 40' |  | 400W MH
400W HPS
1000W MH
1000W HPS
(1) 96" T12HO Strip
(2) 34W T12 Strip
Note on B13: Please select all options from each drop down menu option. Once all fields are selected click the Show me a fixture! button. To search for another criteria set, click the Clear Fields and select from the drop down menus.
Clear Fields
Show me a fixture!

## TER
Indoor REVISED LER Formula
Measure Luminaire "Energy Effectiveness"
Input
Output
| Select Fixture Type | Lowbay
|  | Reflectances |  | RCR #1 |  | RCR #2
| Look for: | 50/30/20 |  | 1 |  | 4
0.33
| Energy Effectiveness Factor (EEF) | 0
| Number of Lamps | 1
Lumens per Lamp
| Total Initial Lamp Lumens (TLL) | 0
Ballast Factor (BF)
Input Wattage
| Target Efficacy Rating (TER) | #DIV/0!
Calculation is in accordance with NEMA STANDARDS PUBLICATION LE 6 – 2008.
Return to HOME
| Please Select | [5 empty] | Please Select
| Cylinder | 80/50/20 | 3 |  |  | 7 | 1
| Downlight, Commercial | 80/50/20 | 1 |  |  | 5 | 2
| Downlight, Residential | 80/50/20 | 1 |  |  | 5 | 3
| Highbay, linear | 50/30/20 | 4 |  |  | 8 | 4
| Highbay, non-linear | 50/30/20 | 4 |  |  | 8 | 5
| Linear industrial | 50/30/20 | 1 |  |  | 8 | 6
| Lowbay | 50/30/20 | 1 |  |  | 4 | 7
| Parking Garage | 30/0/20 | 2 |  |  | 3 | 8
| Recessed, Linear | 80/50/20 | 1 |  |  | 4
| Striplight | 50/30/20 | 1 |  |  | 8
| Surface Mount, Linear | 80/50/20 | 1 |  |  | 4
| Surface Mount, Nonlinear | 80/50/20 | 1 |  |  | 5
| Surface Mount, Residential | 80/50/20 | 1 |  |  | 4
| Suspended, Linear | 80/50/20 | 1 |  |  | 4
| Suspended, Nonlinear | 80/50/20 | 1 |  |  | 5
| Suspended, Residential | 80/50/20 | 1 |  |  | 5
Note on C24: Consult ballast manufacturer catalogs
Note on C26: Pull from Input Watt Finder worksheet if unknown.
Note on G14: These values can be found in the fixture's photometric file and should be % values inputted as 0.00.
Note on I14: These values can be found in the fixture's photometric file and should be % values inputted as 0.00.

## Input Watt Finder
| Insert Logo Here |  | Input Watt Finder
Linear Fluorescent
| T8 Electronic |  |  |  | T5 Electronic |  | T12 Magnetic
| T8 IS Low Ballast Factor 3' |  |  | c349 | T5 Program Rapid Start 2' | c221 | T12 Rapid Start Energy Efficient Magnetic 4' |  | c128
| T8 IS Low Ballast Factor 4' |  |  | c371 | T5 Program Rapid Start 4' | c245
| T8 IS Normal Ballast Factor 2' |  |  | c383 | T5 Program Rapid Start 6' | C255 | T12 Rapid Start Magnetic 3' |  | c140
| T8 IS Normal Ballast Factor 3' |  |  | c395 | T5 Program Rapid Start Step Dimming 4' | c267 | T12 Rapid Start Magnetic 4' |  | c156
| T8 IS Normal Ballast Factor 4' |  |  | c417 |  |  | T12 SL Instant Start Energy Efficient Magnetic 8' |  | c172
| T8 IS High Ballast Factor 4' |  |  | c337 | T5 Program Rapid Start Step Dimming High Output 4' | c279
| T8 PRS Low Ballast Factor 4' |  |  | c351 |  |  | T12 SL Instant Start Magnetic 8' |  | c188
| T8 PRS Normal Ballast Factor 4' |  |  | c479 | T5HO Program Rapid Start 2' | c291 | T12 HO Magnetic 8' |  | c112
| T8 PRS High Ballast Factor 4' |  |  | c465 | T5HO Program Rapid Start 3' | c301 | T12 VHO Energy Efficient Magnetic 8' |  | c198
| T8 Low Output Electronic 8' |  |  | c426 | T5HO Program Rapid Start 4' | c315
| T8 Normal Output Electronic 8' |  |  | c438 |  |  | T12 VHO Magnetic 8' |  | c210
| T8HO Program Rapid Start 8' |  |  | c541 |  |  | U-Lamp T12 Rapid Start |  | c531
| T8 U-Lamp Rapid Start |  |  | c521
| High Intensity Discharge | [5 empty] | Compact Fluorescent
| Magnetic HID |  |  |  | Electronic HID |  | Twin Tube CFL | c400 | c498
| High Pressure Sodium |  |  | c50 | Pulse Start Metal Halide | c96 | Triple Tube CFL |  | c510
| Metal Halide (standard) |  |  | c62 | PAR20 Ceramic Metal Halide |  | Long Twin Tube
| Pulse Start Metal Halide |  |  | c80 | PAR38 Ceramic Metal Halide
PAR20 Ceramic Metal Halide
PAR38 Ceramic Metal Halide
Return to HOME
High Pressure Sodium
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
| 1 | 70W | 90
| 1 | 100W | 125
| 1 | 150W | 188
High Pressure Sodium | 1 | 250W | 300
High Pressure Sodium | 1 | 310W | 365
High Pressure Sodium | 1 | 400W | 464
High Pressure Sodium | 1 | 1000W | 1100
Back to Top
Metal Halide (standard)
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
| 1 | 50W | 72
| 1 | 70W | 94
| 1 | 100W | 125
| 1 | 150W | 180
Metal Halide (standard) | 1 | 175W | 213
Metal Halide (standard) | 1 | 250W | 295
Metal Halide (standard) | 1 | 400W | 455
Metal Halide (standard) | 1 | 1000W | 1085
Back to Top
Pulse Start Metal Halide -Magnetic Ballast
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
Pulse Start -Magnetic Ballast | 1 | 150W | 189
Pulse Start -Magnetic Ballast | 1 | 175W | 208
Pulse Start -Magnetic Ballast | 1 | 200W | 240
Pulse Start -Magnetic Ballast | 1 | 250W | 291
Pulse Start -Magnetic Ballast | 1 | 320W | 368
Pulse Start -Magnetic Ballast | 1 | 350W | 400
Pulse Start -Magnetic Ballast | 1 | 400W | 452
Pulse Start -Magnetic Ballast | 1 | 450W | 404
Pulse Start -Magnetic Ballast | 1 | 750W | 820
Pulse Start -Magnetic Ballast | 1 | 1000W | 1080
Back to Top
Pulse Start Metal Halide - Electronic Ballast
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
Pulse Start-Electronic Ballast | 1 | 70W | 80
Pulse Start-Electronic Ballast | 1 | 100W | 110
Pulse Start-Electronic Ballast | 1 | 150W | 169
Pulse Start-Electronic Ballast | 1 | 175W | 194
Pulse Start-Electronic Ballast | 1 | 250W | 269
Pulse Start-Electronic Ballast | 1 | 320W | 344
Pulse Start-Electronic Ballast | 1 | 350W | 375
Pulse Start-Electronic Ballast | 1 | 400W | 426
Back to Top
T12 HO Magnetic 8'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T12 HO Magnetic | 1 | 110W | 145
T12 HO Magnetic | 1 | 95W | 125
T12 HO Magnetic | 2 | 110W | 253
T12 HO Magnetic | 2 | 95W | 222
T12 HO Magnetic | 3 | 110W | 398
T12 HO Magnetic | 3 | 95W | 347
T12 HO Magnetic | 4 | 110W | 506
T12 HO Magnetic | 4 | 95W | 444
Back to Top
T12 Rapid Start Energy Efficient Magnetic 4'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T12 Rapid Start Energy Efficient Magnetic | 1 | 40W | 50
T12 Rapid Start Energy Efficient Magnetic | 1 | 34W | 42
T12 Rapid Start Energy Efficient Magnetic | 2 | 40W | 82
T12 Rapid Start Energy Efficient Magnetic | 2 | 34W | 73
T12 Rapid Start Energy Efficient Magnetic | 3 | 40W | 132
T12 Rapid Start Energy Efficient Magnetic | 3 | 34W | 115
T12 Rapid Start Energy Efficient Magnetic | 4 | 40W | 164
T12 Rapid Start Energy Efficient Magnetic | 4 | 34W | 146
Back to Top
T12 Rapid Start Magnetic 3'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
| 1 | 25W | 40
| 2 | 25W | 70
| 1 | 30W | 47
| 2 | 30W | 79
Back to Top
T12 Rapid Start Magnetic 4'
| # Lamps | Nominal Wattage | Input Wattage
T12 Rapid Start Magnetic | 1 | 34W | 50
T12 Rapid Start Magnetic | 2 | 34W | 80
T12 Rapid Start Magnetic | 3 | 34W | 130
T12 Rapid Start Magnetic | 4 | 34W | 160
T12 Rapid Start Magnetic | 1 | 40W | 57
T12 Rapid Start Magnetic | 2 | 40W | 94
T12 Rapid Start Magnetic | 3 | 40W | 151
T12 Rapid Start Magnetic | 4 | 40W | 188
Back to Top
T12 SL Instant Start Energy Efficient Magnetic 8'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T12 Slimline Instant Start Energy Efficient Magnetic | 1 | 75W | 92
T12 Slimline Instant Start Energy Efficient Magnetic | 1 | 60W | 76
T12 Slimline Instant Start Energy Efficient Magnetic | 2 | 75W | 158
T12 Slimline Instant Start Energy Efficient Magnetic | 2 | 60W | 126
T12 Slimline Instant Start Energy Efficient Magnetic | 3 | 75W | 250
T12 Slimline Instant Start Energy Efficient Magnetic | 3 | 60W | 202
T12 Slimline Instant Start Energy Efficient Magnetic | 4 | 75W | 316
T12 Slimline Instant Start Energy Efficient Magnetic | 4 | 60W | 252
Back to Top
T12 Slimline Instant Start Magnetic 8'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T12 Slimline Instant Start Magnetic | 1 | 75W | 93
T12 Slimline Instant Start Magnetic | 1 | 60W | 78
T12 Slimline Instant Start Magnetic | 2 | 75W | 158
T12 Slimline Instant Start Magnetic | 2 | 60W | 120
T12 Slimline Instant Start Magnetic | 3 | 75W | 251
T12 Slimline Instant Start Magnetic | 3 | 60W | 198
T12 Slimline Instant Start Magnetic | 4 | 75W | 316
T12 Slimline Instant Start Magnetic | 4 | 60W | 240
Back to Top
T12 VHO Energy Efficient Magnetic 8'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T12 VHO Energy Efficient Magnetic | 1 | 185W | 183
T12 VHO Energy Efficient Magnetic | 2 | 185W | 366
Back to Top
T12 VHO Magnetic 8'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T12 VHO Magnetic | 1 | 215W | 216
T12 VHO Magnetic | 1 | 185W | 198
T12 VHO Magnetic | 2 | 215W | 432
T12 VHO Magnetic | 2 | 185W | 396
Back to Top
T5 Program Rapid Start 2'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
| 1 | 14W | 19
| 2 | 14W | 36
| 3 | 14W | 50
| 1 | 21W | 25
| 2 | 21W | 48
| 3 | 21W | 73
| 4 | 21W | 96
Back to Top
T5 Program Start
T5 Program Start
T5 Program Rapid Start 4'
| # Lamps | Nominal Wattage | Input Wattage
T5 Program Start | 1 | 28W | 33
| 2 | 28W | 64
| 3 | 28W | 97
T5 Program Start | 4 | 28W | 128
Back to Top
T5 Program Rapid Start 6'
| # Lamps | Nominal Wattage | Input Wattage
| 1 | 35W | 41
| 2 | 35W | 80
Back to Top
T5 Program Rapid Start Step Dimming 4'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T5 Program Start Step Dimming | 2 | 28W | 60
T5 Program Start Step Dimming (Dim) | 2 | 28W Dim | 28
T5 Program Start Step Dimming | 4 | 28W | 120
T5 Program Start Step Dimming (Dim) | 4 | 28W Dim | 56
Back to Top
T5 Program Rapid Start 4'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T5 Program Start Step Dimming High Output | 2 | 28W | 71
T5 Program Start Step Dimming High Output | 4 | 28W | 142
T5 Program Start Step Dimming High Output (Dim) | 2 | 28W | 34
T5 Program Start Step Dimming High Output (Dim) | 4 | 28W | 68
Back to Top
T5HO Program Rapid Start 2'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T5HO Program Start | 1 | 24W | 28
T5HO Program Start | 2 | 24W | 52
T5HO Program Start | 3 | 24W | 80
T5HO Program Start | 4 | 24W | 104
Back to Top
T5HO Program Rapid Start 3'
| # Lamps | Nominal Wattage | Input Wattage
| 1 | 39W | 43
| 2 | 39W | 87
Back to Top
T5HO Program Rapid Start 4'
| # Lamps | Nominal Wattage | Input Wattage
T5HO Program Start | 1 | 54W | 62
T5HO Program Start | 2 | 54W | 117
T5HO Program Start | 3 | 54W | 182
T5HO Program Start | 4 | 54W | 229
T5HO Program Start | 6 | 54W | 346
T5HO Program Start | 8 | 54W | 458
Back to Top
T8 Instant Start High Ballast Factor 4'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
| 1 | 28W | 39
| 2 | 28W | 62
T8 Instant Start High Ballast Factor | 3 | 28W | 92
T8 Instant Start High Ballast Factor | 4 | 28W | 124
| 1 | 30W | 43
| 2 | 30W | 68
T8 Instant Start High Ballast Factor | 3 | 30W | 101
T8 Instant Start High Ballast Factor | 4 | 30W | 136
| 1 | 32W | 46
T8 Instant Start High Ballast Factor | 2 | 32W | 73
T8 Instant Start High Ballast Factor | 3 | 32W | 108
T8 Instant Start High Ballast Factor | 4 | 32W | 147
T8 Instant Start High Ballast Factor | 6 | 32W | 220
T8 Instant Start High Ballast Factor | 8 | 32W | 294
Back to Top
T8 Instant Start Low Ballast Factor 3'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T8 Instant Start Low Ballast Factor | 1 | 25W | 21
T8 Instant Start Low Ballast Factor | 2 | 25W | 40
T8 Instant Start Low Ballast Factor | 3 | 25W | 60
T8 Instant Start Low Ballast Factor | 4 | 25W | 80
Back to Top
T8 Instant Start Low Ballast Factor 4'
| # Lamps | Nominal Wattage | Input Wattage
T8 Instant Start Low Ballast Factor | 1 | 28W | 22
T8 Instant Start Low Ballast Factor | 2 | 28W | 44
T8 Instant Start Low Ballast Factor | 3 | 28W | 65
T8 Instant Start Low Ballast Factor | 4 | 28W | 87
T8 Instant Start Low Ballast Factor | 1 | 30W | 24
T8 Instant Start Low Ballast Factor | 2 | 30W | 46
T8 Instant Start Low Ballast Factor | 3 | 30W | 69
T8 Instant Start Low Ballast Factor | 4 | 30W | 92
T8 Instant Start Low Ballast Factor | 1 | 32W | 25
T8 Instant Start Low Ballast Factor | 2 | 32W | 48
T8 Instant Start Low Ballast Factor | 3 | 32W | 73
T8 Instant Start Low Ballast Factor | 4 | 32W | 97
T8 Instant Start Low Ballast Factor | 6 | 32W | 145
T8 Instant Start Low Ballast Factor | 8 | 32W | 194
Back to Top
T8 Instant Start Normal Ballast Factor 2'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
| 1 | 17W | 20
| 2 | 17W | 34
| 3 | 17W | 47
| 4 | 17W | 56
Back to Top
T8 Instant Start Normal Ballast Factor 3'
| # Lamps | Nominal Wattage | Input Wattage
T8 Instant Start Normal Ballast Factor | 1 | 25W | 23
T8 Instant Start Normal Ballast Factor | 2 | 25W | 53
T8 Instant Start Normal Ballast Factor | 3 | 25W | 67
T8 Instant Start Normal Ballast Factor | 4 | 25W | 91
Back to Top
T8 Instant Start Normal Ballast Factor 4'
| # Lamps | Nominal Wattage | Input Wattage
T8 Instant Start Normal Ballast Factor | 1 | 28W | 25
T8 Instant Start Normal Ballast Factor | 2 | 28W | 49
T8 Instant Start Normal Ballast Factor | 3 | 28W | 72
T8 Instant Start Normal Ballast Factor | 4 | 28W | 98
T8 Instant Start Normal Ballast Factor | 1 | 30W | 29
T8 Instant Start Normal Ballast Factor | 2 | 30W | 53
T8 Instant Start Normal Ballast Factor | 3 | 30W | 78
T8 Instant Start Normal Ballast Factor | 4 | 30W | 105
T8 Instant Start Normal Ballast Factor | 1 | 32W | 28
T8 Instant Start Normal Ballast Factor | 2 | 32W | 58
T8 Instant Start Normal Ballast Factor | 3 | 32W | 82
T8 Instant Start Normal Ballast Factor | 4 | 32W | 109
T8 Instant Start Normal Ballast Factor | 6 | 32W | 167
T8 Instant Start Normal Ballast Factor | 8 | 32W | 218
Back to Top
T8 Low Output Electronic 8'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T8 Low Output Electronic (8') | 2 | 59W | 100
Back to Top
T8 Normal Output Electronic 8'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T8 Normal Output Electronic (8') | 1 | 59W | 62
T8 Normal Output Electronic (8') | 2 | 59W | 112
T8 Normal Output Electronic (8') | 3 | 59W | 174
T8 Normal Output Electronic (8') | 4 | 59W | 224
Back to Top
T8 Program Rapid Start Low Ballast Factor 4'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T8 Program Rapid Start Low Ballast Factor | 1 | 32W | 28
T8 Program Rapid Start Low Ballast Factor | 2 | 32W | 44
T8 Program Rapid Start Low Ballast Factor | 3 | 32W | 66
T8 Program Rapid Start Low Ballast Factor | 4 | 32W | 88
T8 Program Rapid Start Low Ballast Factor | 6 | 32W | 132
T8 Program Rapid Start Low Ballast Factor | 8 | 32W | 176
Back to Top
T8 Program Rapid Start High Ballast Factor 4'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T8 Program Rapid Start High Ballast Factor | 1 | 32W | 46
T8 Program Rapid Start High Ballast Factor | 2 | 32W | 74
T8 Program Rapid Start High Ballast Factor | 3 | 32W | 120
T8 Program Rapid Start High Ballast Factor | 4 | 32W | 144
T8 Program Rapid Start High Ballast Factor | 6 | 32W | 218
T8 Program Rapid Start High Ballast Factor | 8 | 32W | 288
Back to Top
T8 Program Rapid Start Normal Ballast Factor 4'
Ballast Type | # Lamps | Nominal Wattage | Input Wattage
T8 Program Rapid Start Normal Ballast Factor | 1 | 32W | 36
T8 Program Rapid Start Normal Ballast Factor | 2 | 32W | 57
T8 Program Rapid Start Normal Ballast Factor | 3 | 32W | 93
T8 Program Rapid Start Normal Ballast Factor | 4 | 32W | 112
T8 Program Rapid Start Normal Ballast Factor | 6 | 32W | 169
T8 Program Rapid Start Normal Ballast Factor | 8 | 32W | 224
Back to Top
Twin Tube CFL
| # Lamps | Nominal Wattage | Input Wattage
| 1 | 5W | 9
| 1 | 7W | 10
| 1 | 9W | 11
| 1 | 13W | 18
| 2 | 13W | 30
| 1 | 18W | 20
| 2 | 18W | 38
Back to Top
Triple Tube CFL
| # Lamps | Nominal Wattage | Input Wattage
| 1 | 26W | 28
| 1 | 32W | 36
| 6 | 32W | 201
| 8 | 32W | 268
| 1 | 32W | 48
| 1 | 42W | 46
| 6 | 42W | 270
| 8 | 42W | 360
Back to Top
Long Twin Tubes (Biax)
| # Lamps | Nominal Wattage | Input Wattage
| 1 | 40 | 44
| 2 | 40 | 71
| 1 | 55 | 51
| 2 | 55 | 100
Back to Top
U-Lamp T8 Rapid Start
| # Lamps | Nominal Wattage | Input Wattage
| 1 | 32 | 35
| 2 | 32 | 73
| 3 | 32 | 108
Back to Top
U-Lamp T12 Rapid Start
| # Lamps | Nominal Wattage | Input Wattage
| 2 | 34W | 60
| 2 | 40W | 70
Back to Top
T8 HO Program Rapid Start 8'
| # Lamps | Nominal Wattage | Input Wattage
| 1 | 86W | 100
| 2 | 86W | 185
Back to Top
PAR20 Metal Halide Electronic
| # Lamps | Nominal Wattage | Input Wattage
| 1 | 39W | 44
Back to Top
PAR38 Metal Halide Electronic
| # Lamps | Nominal Wattage | Input Wattage
| 1 | 70W | 78
| 1 | 100W | 113
Back to Top
PAR20 Metal Halide Magnetic
| # Lamps | Nominal Wattage | Input Wattage
| 1 | 39W | 56
Back to Top
PAR38 Metal Halide Magnetic
| # Lamps | Nominal Wattage | Input Wattage
| 1 | 50W | 72
| 1 | 70W | 94
| 1 | 100W | 125
Back to Top

## Financing
Insert Logo Here
Cash Flow Benefit of Financing
Input
Output
Customer Information
Project Name:
Contact:
Lighting System Details
|  | Number of months: | 30
|  | APR%: | 4.25%
Capital Investment:
|  | Monthly Payment: | 0
Annual Energy Savings:
|  | Monthly Energy Savings: | 0
|  | Monthly Cash Flow Benefit of Financing: | 0
This is only an estimate. Please consult a financial consultant.
Return to HOME
Periods | Rates
12 | 3%
18 | 3.25%
24 | 3.5%
30 | 3.75%
36 | 4%
42 | 4.25%
48 | 4.5%
4.75%
5%
5.25%
5.5%
5.75%
6%
6.25%
6.5%
6.75%
7%
7.25%
7.5%
7.75%
8%
8.25%
8.5%
8.75%
9%
9.25%
9.5%
9.75%
10%
10.25%
10.5%
10.75%
11%
11.25%
11.5%
11.75%
12%
12.25%
12.5%
12.75%
13%
13.25%
13.5%
13.75%
14%
14.25%
14.5%
14.75%
15%
15.25%
15.5%
15.75%
16%
16.25%
16.5%
16.75%
17%
17.25%
17.5%
17.75%
18%
18.25%
18.5%
18.75%
19%
19.25%
19.5%
19.75%
20%

## Website Links
Insert Logo Here
Helpful Web Links
Energy Efficiency Code Requirements
ASHRAE 90.1 | California Energy Commission (CEC)
90.1-2001 | Title 24
90.1-2001 Addenda | Title 20
90.1-2004 | International Dark Sky Association (IDA)
90.1-2004 Addenda | Consortium for Energy Efficiency (CEE)
Lighting Power Density | High Performance Lighting
International Energy Conservation Code (ICC) | Residential Lighting Initiative
Energy Incentives (Accreditation & Financial)
EPAct | U.S. Green Building Council
Commercial Building Tax Deduction Coalition | LEED
Tax Incentives Assistance Project (TIAP) | LEED-EB v2.0
Commercial Lighting Tax Deduction | LEED-NC v2.2
National Electrical Manufacturers Assoc. (NEMA) | ENERGY STAR
Department of Energy (DOE EERE) | Commercial ENERGY STAR
Cooper Lighting EPAct Calculator | Residential ENERGY STAR
Department of Energy
Energy Code Adoption | Rebate Links
Building Codes Assistance Project (BCAP) | State Incentives for Renewables & Efficiency (DSIRE)
Building Energy Code Check | EEI Demand Response Programs
Federal Energy Management Program (FEMP)
Energy Modeling Programs | National Grid
eQUEST | CEE Commercial Lighting Program Summary
VisualDOE | CEE Residential Lighting Program Summary
Industry Associations | Government Agencies & Related Sites
interNat'l Assoc. of Ltg. Maintenance Co. (NALMCO) | Department of Energy Home (DOE)
Edison Electric Institute (EEI) | Environmental Protection Agengcy Home (EPA)
National Electrical Manufacturers' Assoc. (NEMA) | DOE Energy Efficiency & Renewables Home (EERE)
Design Lights Consortium | Federal Energy Management Program (FEMP)
Illuminating Engineering Society of America (IESNA) | Energy Information Administration (EIA)
Nat'l Assoc. of Energy Services Co. (NAESCO)
Lighting Research Center (LRC)
National Lighting Bureau (NLB)
Recyling Resources
Lamprecycle.org | Earth911.org
Lamp Recycling Companies (Lamprecycle.org)
Northeast Waste Management Officials' Association
Listed websites are not affliliated with Cooper Lighting as such Cooper Lighting is not responsible for site content accuracy and timeliness.
Return to TOP
Return to HOME
Note on D19: For clarifications for electrical equipment see the following sections: Material Reuse pg. 51 Recycled Content pg. 53 Regional Materials pg. 55