## 180
3DPIHB-BL-L-BKMT-CL-LF-253033-935 180W 3500K
[8 empty] | CEILING | 80% |  |  |  | 70% |  | 50% |  | 30% |  | 0%
Candlepower Distribution | ANGLE | MEAN CP | LUMENS |  |  |  |  | WALL | 70 | 50 | 30 | 10 | 50 | 10 | 50 | 10 | 50 | 10 | 0
| 0 | 11940.2 | [5 empty] | RCR | Zonal Cavity Method - Effective Floor Cavity Reflectance = 20%
| 5 | 12085.2 |  | Output lumens: |  | 24413 | lm | 0 | 118 | 118 | 118 | 118 | 115 | 115 | 109 | 109 | 103 | 103 | 96
| 10 | 12142.1 | 1149 |  |  |  |  | 1 | 110 | 106 | 103 | 99 | 103 | 97 | 99 | 94 | 94 | 90 | 85
| 15 | 12148.7 |  | Correlated Color Temp: |  | 3500 |  | 2 | 102 | 95 | 90 | 85 | 93 | 84 | 89 | 81 | 85 | 79 | 74
| 20 | 12336.2 | 3433 |  |  |  |  | 3 | 95 | 86 | 79 | 74 | 84 | 73 | 81 | 71 | 77 | 69 | 66
| 25 | 12334.9 |  | Input Watts: |  | 179.9 | W | 4 | 88 | 78 | 70 | 65 | 76 | 64 | 73 | 63 | 71 | 62 | 58
| 30 | 11271.3 | 5481 |  |  |  |  | 5 | 82 | 71 | 63 | 57 | 69 | 57 | 67 | 56 | 65 | 55 | 52
| 35 | 8947.9 |  | Efficacy: |  | 135.7032 | lm/W | 6 | 76 | 65 | 57 | 51 | 64 | 51 | 62 | 50 | 60 | 50 | 47
| 40 | 6219 | 5450 |  |  |  |  | 7 | 71 | 59 | 52 | 46 | 58 | 46 | 57 | 46 | 55 | 45 | 43
| 45 | 4191.8 |  | CRI: |  | 90 | min | 8 | 67 | 55 | 47 | 42 | 54 | 42 | 52 | 41 | 51 | 41 | 39
| 50 | 2954.8 | 3305 |  |  |  |  | 9 | 63 | 51 | 43 | 38 | 50 | 38 | 49 | 38 | 47 | 38 | 36
| 55 | 2743.8 |  | Spacing Criterion: |  | 1.3 |  | 10 | 59 | 47 | 40 | 35 | 47 | 35 | 45 | 35 | 44 | 35 | 33
| 60 | 2127.9 | 2275
| 65 | 1449.3 |  | Beam Angle: |  | 81 | ˚
| 70 | 833.8 | 1480
| 75 | 484.5
| 80 | 333.2 | 568
| 85 | 266.8
| 90 | 218 | 313
Single Unit Data
| ZONAL LUMENS AND PERCENTAGES |  |  | Height to | Initial | Beam
| ZONE | LUMENS | %LUMINAIRE | Lighted Plane | Footcandles | Diameter
| 0-30 | 10063 | 41.22% | 10' | 119.402 | 13 | '
| 0-40 | 15513 | 63.54% | 12' | 82.9181 | 15.6 | '
| 0-60 | 21093 | 86.4% | 14' | 60.9194 | 18.2 | '
| 0-90 | 23454 | 96.07% | 16' | 46.6414 | 20.8 | '
| 0-180 | 24413 | 100% | 18' | 36.8525 | 23.4 | '
| CERTIFIED TEST REPORT NO. |  |  | 1533 *
*Tested using absolute photometry as specified in LM79: IESNA Approved Method for the Electrical and Photometric Measurements of Solid-State Lighting Products.
*Tested using absolute photometry as specified in LM79: IESNA Approved Method for the Electrical and Photometric Measurements of Solid-State Lighting Products.

## 220
3DPIHB-BL-L-BKMT-CL-LF-253033-935 220W 3500K
[8 empty] | CEILING | 80% |  |  |  | 70% |  | 50% |  | 30% |  | 0%
Candlepower Distribution | ANGLE | MEAN CP | LUMENS |  |  |  |  | WALL | 70 | 50 | 30 | 10 | 50 | 10 | 50 | 10 | 50 | 10 | 0
| 0 | 14102.3 | [5 empty] | RCR | Zonal Cavity Method - Effective Floor Cavity Reflectance = 20%
| 5 | 14270 |  | Output lumens: |  | 28888 | lm | 0 | 118 | 118 | 118 | 118 | 115 | 115 | 109 | 109 | 103 | 103 | 96
| 10 | 14344.9 | 1357 |  |  |  |  | 1 | 110 | 106 | 103 | 99 | 103 | 97 | 99 | 94 | 94 | 90 | 85
| 15 | 14341.2 |  | Correlated Color Temp: |  | 3500 |  | 2 | 102 | 95 | 90 | 85 | 93 | 84 | 89 | 81 | 85 | 79 | 74
| 20 | 14552.4 | 4054 |  |  |  |  | 3 | 95 | 86 | 79 | 74 | 84 | 73 | 81 | 71 | 77 | 69 | 66
| 25 | 14545.2 |  | Input Watts: |  | 219.3 | W | 4 | 88 | 78 | 70 | 65 | 76 | 64 | 73 | 63 | 71 | 62 | 58
| 30 | 13270.3 | 6473 |  |  |  |  | 5 | 82 | 71 | 63 | 57 | 69 | 57 | 67 | 56 | 65 | 55 | 52
| 35 | 10530.7 |  | Efficacy: |  | 131.7282 | lm/W | 6 | 76 | 65 | 57 | 51 | 64 | 51 | 62 | 50 | 60 | 50 | 47
| 40 | 7311 | 6439 |  |  |  |  | 7 | 71 | 59 | 52 | 46 | 58 | 46 | 57 | 46 | 55 | 45 | 43
| 45 | 4937.4 |  | CRI: |  | 90 | min | 8 | 67 | 55 | 47 | 42 | 54 | 42 | 52 | 41 | 51 | 41 | 39
| 50 | 3498.6 | 3903 |  |  |  |  | 9 | 63 | 51 | 43 | 38 | 50 | 38 | 49 | 38 | 47 | 38 | 36
| 55 | 3266 |  | Spacing Criterion: |  | 1.3 |  | 10 | 59 | 47 | 40 | 35 | 47 | 35 | 45 | 35 | 44 | 35 | 33
| 60 | 2528.2 | 2704
| 65 | 1722.8 |  | Beam Angle: |  | 81 | ˚
| 70 | 992.4 | 1765
| 75 | 580.1
| 80 | 397 | 680
| 85 | 317.8
| 90 | 259.7 | 373
Single Unit Data
| ZONAL LUMENS AND PERCENTAGES |  |  | Height to | Initial | Beam
| ZONE | LUMENS | %LUMINAIRE | Lighted Plane | Footcandles | Diameter
| 0-30 | 11884 | 41.14% | 12' | 97.9326 | 15.6 | '
| 0-40 | 18322 | 63.42% | 14' | 71.9505 | 18.2 | '
| 0-60 | 24929 | 86.3% | 16' | 55.0871 | 20.8 | '
| 0-90 | 27746 | 96.05% | 18' | 43.5256 | 23.4 | '
| 0-180 | 28888 | 100% | 20' | 35.2557 | 26 | '
| CERTIFIED TEST REPORT NO. |  |  | 1533 *
*Tested using absolute photometry as specified in LM79: IESNA Approved Method for the Electrical and Photometric Measurements of Solid-State Lighting Products.
*Tested using absolute photometry as specified in LM79: IESNA Approved Method for the Electrical and Photometric Measurements of Solid-State Lighting Products.

## 240
3DPIHB-BL-L-BKMT-CL-LF-253033-935 240W 3500K
[8 empty] | CEILING | 80% |  |  |  | 70% |  | 50% |  | 30% |  | 0%
Candlepower Distribution | ANGLE | MEAN CP | LUMENS |  |  |  |  | WALL | 70 | 50 | 30 | 10 | 50 | 10 | 50 | 10 | 50 | 10 | 0
| 0 | 15059.5 | [5 empty] | RCR | Zonal Cavity Method - Effective Floor Cavity Reflectance = 20%
| 5 | 15153.4 |  | Output lumens: |  | 30900 | lm | 0 | 118 | 118 | 118 | 118 | 115 | 115 | 109 | 109 | 103 | 103 | 96
| 10 | 15229 | 1449 |  |  |  |  | 1 | 110 | 106 | 103 | 99 | 103 | 97 | 99 | 94 | 94 | 90 | 85
| 15 | 15224 |  | Correlated Color Temp: |  | 3500 |  | 2 | 102 | 95 | 90 | 85 | 93 | 84 | 89 | 81 | 85 | 79 | 74
| 20 | 15441.5 | 4328 |  |  |  |  | 3 | 95 | 86 | 79 | 74 | 84 | 73 | 81 | 71 | 77 | 69 | 66
| 25 | 15456.4 |  | Input Watts: |  | 237.2 | W | 4 | 88 | 78 | 70 | 65 | 76 | 64 | 73 | 63 | 71 | 62 | 58
| 30 | 14211.3 | 6913 |  |  |  |  | 5 | 82 | 71 | 63 | 57 | 69 | 57 | 67 | 56 | 65 | 55 | 52
| 35 | 11363.1 |  | Efficacy: |  | 130.2698 | lm/W | 6 | 76 | 65 | 57 | 51 | 64 | 51 | 62 | 50 | 60 | 50 | 47
| 40 | 7935.9 | 6883 |  |  |  |  | 7 | 71 | 59 | 52 | 46 | 58 | 46 | 57 | 46 | 55 | 45 | 43
| 45 | 5365.2 |  | CRI: |  | 90 | min | 8 | 67 | 55 | 47 | 42 | 54 | 42 | 52 | 41 | 51 | 41 | 39
| 50 | 3771.2 | 4173 |  |  |  |  | 9 | 63 | 51 | 43 | 38 | 50 | 38 | 49 | 38 | 47 | 38 | 36
| 55 | 3517.3 |  | Spacing Criterion: |  | 1.3 |  | 10 | 59 | 47 | 40 | 35 | 47 | 35 | 45 | 35 | 44 | 35 | 33
| 60 | 2743.1 | 2899
| 65 | 1887.5 |  | Beam Angle: |  | 81 | ˚
| 70 | 1093.8 | 1900
| 75 | 636.3
| 80 | 431.7 | 732
| 85 | 343.8
| 90 | 279.8 | 401
Single Unit Data
| ZONAL LUMENS AND PERCENTAGES |  |  | Height to | Initial | Beam
| ZONE | LUMENS | %LUMINAIRE | Lighted Plane | Footcandles | Diameter
| 0-30 | 12690 | 41.07% | 12' | 104.5799 | 15.6 | '
| 0-40 | 19573 | 63.34% | 14' | 76.8342 | 18.2 | '
| 0-60 | 26644 | 86.23% | 16' | 58.8262 | 20.8 | '
| 0-90 | 29677 | 96.04% | 18' | 46.4799 | 23.4 | '
| 0-180 | 30900 | 100% | 20' | 37.6487 | 26 | '
| CERTIFIED TEST REPORT NO. |  |  | 1533 *
*Tested using absolute photometry as specified in LM79: IESNA Approved Method for the Electrical and Photometric Measurements of Solid-State Lighting Products.
*Tested using absolute photometry as specified in LM79: IESNA Approved Method for the Electrical and Photometric Measurements of Solid-State Lighting Products.

## Wattage (hidden)
Wattage: | 26.6 w
watts | 26.6
Wattage2: | 39.5 w
watts2 | 39.5